## Summary
Summary of results for tank connected to each node
| Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Pumping Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
0 | J65 | 5.91 | 126.62 | 71.22 | 71.22 | € 1,188.66 | 2830.14 | 310.1 | 300.1 | 804.56 | 2.09 | 22 | R_TIBAR_2 | [] | € 676,560.33 | € 1,145,029.22 | € 519,358.76 | € 2,340,948.31 | € 27,889.95 | € 204,094.54 | € 665,844.47
1 | J66 | 5.13 | 126.38 | 71.22 | 71.22 | € 1,186.45 | 2824.88 | 309.64 | 279.64 | 804.56 | 2.1 | 22 | R_TIBAR_2 | [] | € 676,560.33 | € 1,095,658.21 | € 1,372.50 | € 1,773,591.04 | € 24,905.05 | € 154,629.75 | € 612,588.96
2 | J67 | 5.64 | 126.55 | 71.22 | 71.21 | € 1,187.93 | 2828.39 | 309.48 | 299.48 | 804.56 | 2.1 | 21 | R_TIBAR_2 | [] | € 676,560.33 | € 1,143,535.10 | € 227,064.88 | € 2,047,160.31 | € 26,416.52 | € 178,480.76 | € 638,490.19
3 | J69 | 8.09 | 126.47 | 71.22 | 71.23 | € 1,187.31 | 2826.93 | 311.78 | 191.78 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 883,592.82 | € 97,085.00 | € 1,657,238.15 | € 23,687.09 | € 144,485.57 | € 601,541.03
4 | J70 | 6.01 | 126.11 | 71.22 | 71.22 | € 1,183.82 | 2818.62 | 311.22 | 301.22 | 804.56 | 2.1 | 22 | R_TIBAR_2 | [] | € 676,560.33 | € 1,147,736.96 | € 1,076,734.30 | € 2,901,031.59 | € 30,698.49 | € 252,925.15 | € 715,717.63
5 | J71 | 5.35 | 126.04 | 71.22 | 71.23 | € 1,183.20 | 2817.15 | 311.34 | 301.34 | 804.56 | 2.1 | 22 | R_TIBAR_2 | [] | € 676,560.33 | € 1,148,017.75 | € 898,169.90 | € 2,722,747.98 | € 29,807.91 | € 237,381.58 | € 699,059.17
6 | J72 | 4.9 | 126 | 71.22 | 71.23 | € 1,182.91 | 2816.45 | 311.59 | 281.59 | 804.56 | 2.09 | 22 | R_TIBAR_2 | [] | € 676,560.33 | € 1,100,360.95 | € 695,587.04 | € 2,472,508.33 | € 28,413.74 | € 215,564.54 | € 675,739.62
7 | J73 | 4.63 | 125.94 | 71.22 | 71.24 | € 1,182.33 | 2815.08 | 311.77 | 281.77 | 804.56 | 2.09 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 1,100,779.93 | € 551,061.50 | € 2,328,401.76 | € 27,694.47 | € 203,000.68 | € 662,246.92
8 | J139 | 3.18 | 126 | 71.22 | 71.24 | € 1,182.87 | 2816.37 | 312.99 | 232.99 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 983,046.50 | € 551,061.50 | € 2,210,668.34 | € 26,752.60 | € 192,736.14 | € 651,237.68
9 | TIBAR_PORT | 6.41 | 126.3 | 71.22 | 71.21 | € 1,185.44 | 2822.47 | 310.63 | 300.63 | 804.56 | 2.1 | 21 | R_TIBAR_2 | [] | € 676,560.33 | € 1,146,314.14 | € 994,388.31 | € 2,817,262.78 | € 30,275.37 | € 245,621.81 | € 708,581.34
10 | R_TIBAR_2 | 1.05 | 128.58 | 71.22 | 71.24 | € 1,207.09 | 2874.03 | 320.1 | 0.1 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 420,925.72 | € 1,372.50 | € 1,098,858.55 | € 19,507.19 | € 95,803.50 | € 555,899.48
11 | R_TIBAR_3 | 2.63 | 126.01 | 71.22 | 71.24 | € 1,183.01 | 2816.68 | 313.49 | 153.49 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 791,168.02 | € 551,061.50 | € 2,018,789.85 | € 25,217.57 | € 176,007.30 | € 633,021.77
12 | R_TIBAR_4 | 2.66 | 126.01 | 71.22 | 71.24 | € 1,182.96 | 2816.57 | 313.47 | 153.47 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 791,119.00 | € 551,061.50 | € 2,018,740.83 | € 25,217.18 | € 176,003.03 | € 633,000.23
13 | ETA_COMORO | 0 | 132.74 | 71.22 | 71.24 | € 1,246.08 | 2966.86 | 329.19 | 229.19 | 804.56 | 2.1 | 7 | R_TIBAR_2 | [] | € 676,560.33 | € 973,886.56 | € 1,372.50 | € 1,651,819.39 | € 23,930.87 | € 144,013.14 | € 622,763.49
14 | R_TIBAR_1 | 1 | 128.55 | 71.22 | 71.24 | € 1,206.80 | 2873.32 | 320.42 | 0.42 | 804.56 | 2.09 | 22 | R_TIBAR_2 | [] | € 676,560.33 | € 421,702.90 | € 1,372.50 | € 1,099,635.74 | € 19,513.41 | € 95,871.25 | € 555,864.85
15 | prv2 | 3.18 | 126 | 71.22 | 71.24 | € 1,182.90 | 2816.42 | 312.99 | 232.99 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 983,056.81 | € 551,061.50 | € 2,210,678.65 | € 26,752.68 | € 192,737.04 | € 651,246.88
16 | prv3 | 4.63 | 124.83 | 71.22 | 71.24 | € 1,171.89 | 2790.21 | 314.8 | 284.8 | 804.56 | 2.1 | 23 | R_TIBAR_2 | [] | € 676,560.33 | € 1,108,105.63 | € 695,716.50 | € 2,480,382.46 | € 28,476.35 | € 216,251.05 | € 672,466.40

## J65
This sheet contains the results for tank connected to node: J65
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.62 | m |  | Minimum Pressure | 2.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.22 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,188.66 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2830.14 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 310.1 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 300.1 | m above nearest node |  | Tank Investment Cost | € 1,145,029.22
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 519,358.76
|  |  |  | Total Investment Cost | € 2,340,948.31
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 160 | 52 | 19678.36
P25 | 54.9 | 894.02 | 125 | 34 | 30396.68
P27 | 110.2 | 622.86 | 140 | 41 | 25537.26
P28 | 54.9 | 793.82 | 110 | 28 | 22226.96
P29 | 123.4 | 733.42 | 315 | 190 | 139349.8
P30 | 198.2 | 903.77 | 315 | 190 | 171716.3
P31 | 220.4 | 574.11 | 315 | 190 | 109080.9
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J66
This sheet contains the results for tank connected to node: J66
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.38 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.22 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,186.45 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2824.88 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 309.64 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 279.64 | m above nearest node |  | Tank Investment Cost | € 1,095,658.21
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 1,773,591.04
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J67
This sheet contains the results for tank connected to node: J67
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.55 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 71.21 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,187.93 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2828.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 309.48 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 299.48 | m above nearest node |  | Tank Investment Cost | € 1,143,535.10
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 227,064.88
|  |  |  | Total Investment Cost | € 2,047,160.31
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 63 | 14 | 5298.02
P25 | 54.9 | 894.02 | 110 | 28 | 25032.56
P26 | 176.2 | 1028.22 | 315 | 190 | 195361.8
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J69
This sheet contains the results for tank connected to node: J69
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.47 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.23 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,187.31 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2826.93 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 311.78 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 191.78 | m above nearest node |  | Tank Investment Cost | € 883,592.82
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 97,085.00
|  |  |  | Total Investment Cost | € 1,657,238.15
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P171 | 54.9 | 503.75 | 315 | 190 | 95712.5
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J70
This sheet contains the results for tank connected to node: J70
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.11 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.22 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,183.82 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2818.62 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 311.22 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 301.22 | m above nearest node |  | Tank Investment Cost | € 1,147,736.96
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,076,734.30
|  |  |  | Total Investment Cost | € 2,901,031.59
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 160 | 52 | 19678.36
P25 | 54.9 | 894.02 | 160 | 52 | 46489.04
P27 | 110.2 | 622.86 | 315 | 190 | 118343.4
P28 | 54.9 | 793.82 | 110 | 28 | 22226.96
P29 | 123.4 | 733.42 | 160 | 52 | 38137.84
P30 | 198.2 | 903.77 | 315 | 190 | 171716.3
P31 | 220.4 | 574.11 | 315 | 190 | 109080.9
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J71
This sheet contains the results for tank connected to node: J71
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.04 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.23 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,183.20 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2817.15 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 311.34 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 301.34 | m above nearest node |  | Tank Investment Cost | € 1,148,017.75
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 898,169.90
|  |  |  | Total Investment Cost | € 2,722,747.98
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P25 | 54.9 | 894.02 | 110 | 28 | 25032.56
P28 | 54.9 | 793.82 | 160 | 52 | 41278.64
P30 | 198.2 | 903.77 | 315 | 190 | 171716.3
P31 | 220.4 | 574.11 | 315 | 190 | 109080.9
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J72
This sheet contains the results for tank connected to node: J72
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126 | m |  | Minimum Pressure | 2.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.23 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,182.91 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2816.45 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 311.59 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 281.59 | m above nearest node |  | Tank Investment Cost | € 1,100,360.95
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 695,587.04
|  |  |  | Total Investment Cost | € 2,472,508.33
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P25 | 54.9 | 894.02 | 90 | 21 | 18774.42
P28 | 54.9 | 793.82 | 90 | 21 | 16670.22
P31 | 220.4 | 574.11 | 315 | 190 | 109080.9
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J73
This sheet contains the results for tank connected to node: J73
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 125.94 | m |  | Minimum Pressure | 2.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,182.33 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2815.08 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 311.77 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 281.77 | m above nearest node |  | Tank Investment Cost | € 1,100,779.93
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 551,061.50
|  |  |  | Total Investment Cost | € 2,328,401.76
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## J139
This sheet contains the results for tank connected to node: J139
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,182.87 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2816.37 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 312.99 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 232.99 | m above nearest node |  | Tank Investment Cost | € 983,046.50
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 551,061.50
|  |  |  | Total Investment Cost | € 2,210,668.34
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## TIBAR_PORT
This sheet contains the results for tank connected to node: TIBAR_PORT
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.3 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 71.21 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,185.44 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2822.47 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 310.63 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 300.63 | m above nearest node |  | Tank Investment Cost | € 1,146,314.14
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 994,388.31
|  |  |  | Total Investment Cost | € 2,817,262.78
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 90 | 21 | 7947.03
P25 | 54.9 | 894.02 | 125 | 34 | 30396.68
P26 | 176.2 | 1028.22 | 315 | 190 | 195361.8
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
P176 | 123.4 | 1103.27 | 315 | 190 | 209621.3
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## R_TIBAR_2
This sheet contains the results for tank connected to node: R_TIBAR_2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 128.58 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,207.09 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2874.03 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 320.1 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 0.1 | m above nearest node |  | Tank Investment Cost | € 420,925.72
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 1,098,858.55
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## R_TIBAR_3
This sheet contains the results for tank connected to node: R_TIBAR_3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.01 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,183.01 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2816.68 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 313.49 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 153.49 | m above nearest node |  | Tank Investment Cost | € 791,168.02
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 551,061.50
|  |  |  | Total Investment Cost | € 2,018,789.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## R_TIBAR_4
This sheet contains the results for tank connected to node: R_TIBAR_4
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126.01 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,182.96 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2816.57 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 313.47 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 153.47 | m above nearest node |  | Tank Investment Cost | € 791,119.00
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 551,061.50
|  |  |  | Total Investment Cost | € 2,018,740.83
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## ETA_COMORO
This sheet contains the results for tank connected to node: ETA_COMORO
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 132.74 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,246.08 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2966.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 329.19 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 229.19 | m above nearest node |  | Tank Investment Cost | € 973,886.56
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 1,651,819.39
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## R_TIBAR_1
This sheet contains the results for tank connected to node: R_TIBAR_1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 128.55 | m |  | Minimum Pressure | 2.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,206.80 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2873.32 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 320.42 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 0.42 | m above nearest node |  | Tank Investment Cost | € 421,702.90
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 1,099,635.74
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## prv2
This sheet contains the results for tank connected to node: prv2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 126 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,182.90 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2816.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 312.99 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 232.99 | m above nearest node |  | Tank Investment Cost | € 983,056.81
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 551,061.50
|  |  |  | Total Investment Cost | € 2,210,678.65
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## prv3
This sheet contains the results for tank connected to node: prv3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 124.83 | m |  | Minimum Pressure | 2.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Pumping Cost: | € 1,171.89 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 2790.21 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 314.8 | m above sea level |  | Pump Investment Cost | € 676,560.33
Tank height above ground | 284.8 | m above nearest node |  | Tank Investment Cost | € 1,108,105.63
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 695,716.50
|  |  |  | Total Investment Cost | € 2,480,382.46
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5