## Summary
Summary of results for tank connected to each node
1
Column1 | Column2 | Node | Parameter | Value | Units | Node | Duty Head | Duty Flow | Actual average pumped flow: | Cost: | Energy: | Tank Elevation | Tank height above ground | Tank volume | Minimum Pressure | Critical Hour | Critical Node | Critical Pipes | Pump Cost | Tank Cost | Total Pipe Replacement Cost | Total Investment Cost
0 | Summaryfor | Summary | for | node: | a01 | a01 | 46.57 | 102.81 | 102.79 | €225.43 | 1502.89 | 42.62 | 42.62 | 1469.6 | 20.1 | 6 | e05 | [] | €907,505.33 | €708,340.50 | €526,034.00 | 2141879.83
1 | a01Duty Head | a01 | Duty Head | 46.57 | m | a02 | 44.58 | 102.81 | 102.78 | €215.78 | 1438.55 | 39.57 | 39.57 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €694,890.21 | €526,034.00 | 2128429.53
2 | a01Duty Flow | a01 | Duty Flow | 102.81 | L/s | a03 | 44.17 | 102.81 | 102.74 | €213.81 | 1425.39 | 39.02 | 39.02 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €692,488.29 | €701,174.00 | 2301167.61
3 | a01Actual average pumped flow: | a01 | Actual average pumped flow: | 102.79 | L/s | a04 | 43.58 | 102.81 | 102.78 | €210.96 | 1406.39 | 38.04 | 38.04 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €688,136.32 | €526,034.00 | 2121675.65
4 | a01Cost: | a01 | Cost: | €225.43 | Europerday | a05 | 43.62 | 102.81 | 102.75 | €211.17 | 1407.77 | 38.21 | 38.21 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €688,891.78 | €695,279.00 | 2291676.11
5 | a01Energy: | a01 | Energy: | 1502.89 | kWh/day | a06 | 43.12 | 102.81 | 102.78 | €208.71 | 1391.42 | 37.33 | 37.33 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €685,018.03 | €526,034.00 | 2118557.36
6 | a01Tank Elevation | a01 | Tank Elevation | 42.62 | m above sea level | a07 | 42.82 | 102.81 | 102.78 | €207.26 | 1381.75 | 36.87 | 36.87 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €682,991.43 | €526,034.00 | 2116530.76
7 | a01Tank height above ground | a01 | Tank height above ground | 42.62 | m above nearest node | a08 | 42.74 | 102.81 | 102.76 | €206.89 | 1379.28 | 36.77 | 36.77 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €682,568.77 | €790,869.00 | 2380943.1
8 | a01Tank volume | a01 | Tank volume | 1469.6 | m3 | a09 | 43 | 102.81 | 102.77 | €208.03 | 1386.87 | 36.87 | 36.87 | 1469.6 | 20.1 | 6 | e05 | [] | €907,505.33 | €682,981.52 | €833,700.00 | 2424186.85
9 | a01Minimum Pressure | a01 | Minimum Pressure | 20.1 | mwc | a10 | 42.8 | 102.81 | 102.8 | €207.06 | 1380.41 | 36.76 | 36.76 | 1469.6 | 20.1 | 6 | e05 | [] | €907,505.33 | €682,504.44 | €890,584.00 | 2480593.77
10 | a01Critical Hour | a01 | Critical Hour | 6 | hrs | a11 | 43.6 | 102.81 | 102.73 | €210.96 | 1406.39 | 37.5 | 37.5 | 1469.6 | 20.1 | 6 | e05 | [] | €907,505.33 | €685,759.83 | €901,659.00 | 2494924.16
11 | a01Critical Node | a01 | Critical Node | e05 | Node | a12 | 43.96 | 102.81 | 102.74 | €212.71 | 1418.09 | 37.94 | 37.94 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €687,727.54 | €942,969.00 | 2538201.87
12 | a01Critical Pipes | a01 | Critical Pipes | [] | Unit headloss >10m/km | a13 | 44.2 | 102.81 | 102.81 | €213.77 | 1425.13 | 38.12 | 38.12 | 1469.6 | 20.01 | 6 | e05 | [] | €907,505.33 | €688,490.89 | €1,002,279.00 | 2598275.21
13 | a01Pump Cost | a01 | Pump Cost | €907,505.33 | Capital Investment | a14 | 41.99 | 102.81 | 102.81 | €203.27 | 1355.12 | 35.6 | 35.6 | 1469.6 | 20.04 | 6 | e05 | [] | €907,505.33 | €677,414.25 | €526,034.00 | 2110953.58
14 | a01Tank Cost | a01 | Tank Cost | €708,340.50 | Capital Investment | a15 | 42.78 | 102.81 | 102.73 | €207.06 | 1380.4 | 36.55 | 36.55 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €681,594.94 | €813,504.00 | 2402604.27
15 | a01Total Pipe Replacement Cost | a01 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment | a16 | 41.79 | 102.81 | 102.78 | €202.26 | 1348.42 | 35.27 | 35.27 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €675,938.21 | €526,034.00 | 2109477.54
16 | a01Total Investment Cost | a01 | Total Investment Cost | €2,141,879.83 | Grand Total | a17 | 41.09 | 102.81 | 102.75 | €198.90 | 1325.99 | 34.5 | 34.5 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €672,548.31 | €695,444.00 | 2275497.63
17 | ------ | --- | --- | --- | --- | a18 | 41.73 | 102.81 | 102.81 | €201.85 | 1345.67 | 35 | 35 | 1469.6 | 20.08 | 6 | e05 | [] | €907,505.33 | €674,742.30 | €730,754.00 | 2313001.63
18 | Summaryfor | Summary | for | node: | a02 | a19 | 39.54 | 102.81 | 102.78 | €191.32 | 1275.49 | 32.75 | 32.75 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €664,811.36 | €628,994.00 | 2201310.69
19 | a02Duty Head | a02 | Duty Head | 44.58 | m | a20 | 39.76 | 102.81 | 102.77 | €192.40 | 1282.69 | 33.08 | 33.08 | 1469.6 | 20.09 | 16 | e05 | [] | €907,505.33 | €666,282.10 | €823,739.00 | 2397526.43
20 | a02Duty Flow | a02 | Duty Flow | 102.81 | L/s | a21 | 40.09 | 102.81 | 102.74 | €194.02 | 1293.46 | 33.43 | 33.43 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €667,817.26 | €892,709.00 | 2468031.59
21 | a02Actual average pumped flow: | a02 | Actual average pumped flow: | 102.78 | L/s | b01 | 37.16 | 102.81 | 102.75 | €179.83 | 1198.84 | 30.1 | 30.1 | 1469.6 | 20.09 | 16 | e05 | [] | €907,505.33 | €653,165.04 | €762,914.00 | 2323584.37
22 | a02Cost: | a02 | Cost: | €215.78 | Europerday | b02 | 37.29 | 102.81 | 102.72 | €180.42 | 1202.83 | 30.17 | 30.17 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €653,460.44 | €901,514.00 | 2462479.77
23 | a02Energy: | a02 | Energy: | 1438.55 | kWh/day | b03 | 37.41 | 102.81 | 102.81 | €180.97 | 1206.44 | 30.17 | 30.17 | 1469.6 | 20.09 | 16 | e05 | [] | €907,505.33 | €653,475.24 | €990,794.00 | 2551774.57
24 | a02Tank Elevation | a02 | Tank Elevation | 39.57 | m above sea level | b04 | 37.55 | 102.81 | 102.76 | €181.61 | 1210.74 | 30.31 | 30.31 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €654,079.77 | €1,123,368.00 | 2684953.1
25 | a02Tank height above ground | a02 | Tank height above ground | 39.57 | m above nearest node | b05 | 38.37 | 102.81 | 102.81 | €185.41 | 1236.1 | 30.92 | 30.92 | 1469.6 | 19.95 | 16 | e05 | [] | €907,505.33 | €656,758.23 | €1,230,660.00 | 2794923.56
26 | a02Tank volume | a02 | Tank volume | 1469.6 | m3 | b06 | 37.62 | 102.81 | 102.78 | €181.93 | 1212.84 | 30.36 | 30.36 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €654,282.57 | €1,175,820.00 | 2737607.89
27 | a02Minimum Pressure | a02 | Minimum Pressure | 20.09 | mwc | b07 | 38.34 | 102.81 | 102.81 | €185.29 | 1235.26 | 30.94 | 30.94 | 1469.6 | 19.99 | 16 | e05 | [] | €907,505.33 | €656,852.15 | €1,195,773.00 | 2760130.47
28 | a02Critical Hour | a02 | Critical Hour | 6 | hrs | b08 | 38.67 | 102.81 | 102.74 | €186.82 | 1245.47 | 31.25 | 31.25 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €658,217.49 | €1,321,665.00 | 2887387.82
29 | a02Critical Node | a02 | Critical Node | e05 | Node | b09 | 37.59 | 102.81 | 102.78 | €181.79 | 1211.95 | 30.34 | 30.34 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €654,219.18 | €1,175,778.00 | 2737502.51
30 | a02Critical Pipes | a02 | Critical Pipes | [] | Unit headloss >10m/km | b10 | 38.34 | 102.81 | 102.81 | €185.29 | 1235.28 | 31 | 31 | 1469.6 | 19.99 | 16 | e05 | [] | €907,505.33 | €657,119.84 | €1,180,008.00 | 2744633.17
31 | a02Pump Cost | a02 | Pump Cost | €907,505.33 | Capital Investment | b11 | 40.13 | 102.81 | 102.84 | €193.64 | 1290.91 | 32.17 | 32.17 | 1469.6 | 20.09 | 6 | e05 | [] | €907,505.33 | €662,259.66 | €1,231,931.00 | 2801695.99
32 | a02Tank Cost | a02 | Tank Cost | €694,890.21 | Capital Investment | b12 | 38.68 | 102.81 | 102.78 | €186.88 | 1245.86 | 31.21 | 31.21 | 1469.6 | 20.1 | 16 | e05 | [] | €907,505.33 | €658,026.79 | €1,415,572.00 | 2981104.11
33 | a02Total Pipe Replacement Cost | a02 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment | c01 | 34 | 102.81 | 102.78 | €164.41 | 1096.04 | 26.57 | 26.57 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €637,571.18 | €1,049,974.00 | 2595050.51
34 | a02Total Investment Cost | a02 | Total Investment Cost | €2,128,429.53 | Grand Total | c02 | 34.09 | 102.81 | 102.77 | €164.84 | 1098.95 | 26.65 | 26.65 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €637,940.03 | €1,198,284.00 | 2743729.36
35 | ------ | --- | --- | --- | --- | c03 | 34.74 | 102.81 | 102.81 | €167.85 | 1119.03 | 27.16 | 27.16 | 1469.6 | 20.01 | 16 | b12 | [] | €907,505.33 | €640,173.89 | €1,269,619.00 | 2817298.21
36 | Summaryfor | Summary | for | node: | a03 | c04 | 34.91 | 102.81 | 102.78 | €168.69 | 1124.6 | 27.33 | 27.33 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €640,915.06 | €1,332,844.00 | 2881264.38
37 | a03Duty Head | a03 | Duty Head | 44.17 | m | c05 | 34.22 | 102.81 | 102.78 | €165.43 | 1102.86 | 26.67 | 26.67 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €638,022.14 | €1,296,246.00 | 2841773.47
38 | a03Duty Flow | a03 | Duty Flow | 102.81 | L/s | c06 | 35 | 102.81 | 102.81 | €169.03 | 1126.89 | 27.11 | 27.11 | 1469.6 | 19.99 | 16 | b12 | [] | €907,505.33 | €639,955.10 | €1,317,184.00 | 2864644.43
39 | a03Actual average pumped flow: | a03 | Actual average pumped flow: | 102.74 | L/s | c07 | 35.38 | 102.81 | 102.77 | €170.84 | 1138.92 | 27.56 | 27.56 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €641,962.19 | €1,336,354.00 | 2885821.52
40 | a03Cost: | a03 | Cost: | €213.81 | Europerday | d01 | 34.22 | 102.81 | 102.78 | €165.46 | 1103.05 | 26.75 | 26.75 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €638,392.26 | €1,229,074.00 | 2774971.58
41 | a03Energy: | a03 | Energy: | 1425.39 | kWh/day | d02 | 35.79 | 102.81 | 102.84 | €172.84 | 1152.27 | 28.15 | 28.15 | 1469.6 | 20.09 | 6 | b12 | [] | €907,505.33 | €644,542.28 | €1,226,014.00 | 2778061.61
42 | a03Tank Elevation | a03 | Tank Elevation | 39.02 | m above sea level | d03 | 34.34 | 102.81 | 102.79 | €166.02 | 1106.78 | 26.86 | 26.86 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €638,849.57 | €1,322,224.00 | 2868578.9
43 | a03Tank height above ground | a03 | Tank height above ground | 39.02 | m above nearest node | d04 | 42 | 102.81 | 102.87 | €202.09 | 1347.27 | 31.06 | 31.06 | 1469.6 | 19.99 | 6 | b12 | [] | €907,505.33 | €657,371.28 | €1,150,864.00 | 2715740.6
44 | a03Tank volume | a03 | Tank volume | 1469.6 | m3 | d05 | 34.43 | 102.81 | 102.78 | €166.43 | 1109.53 | 26.94 | 26.94 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €639,206.90 | €1,438,864.00 | 2985576.23
45 | a03Minimum Pressure | a03 | Minimum Pressure | 20.09 | mwc | d06 | 36.41 | 102.81 | 102.84 | €175.77 | 1171.81 | 28.66 | 28.66 | 1469.6 | 20.09 | 6 | b12 | [] | €907,505.33 | €646,798.73 | €1,414,214.00 | 2968518.06
46 | a03Critical Hour | a03 | Critical Hour | 6 | hrs | d07 | 37.03 | 102.81 | 102.75 | €178.64 | 1190.94 | 29.32 | 29.32 | 1469.6 | 20.1 | 6 | b12 | [] | €907,505.33 | €649,715.93 | €1,490,434.00 | 3047655.26
47 | a03Critical Node | a03 | Critical Node | e05 | Node | d08 | 37.53 | 102.81 | 102.85 | €181.07 | 1207.15 | 29.74 | 29.74 | 1469.6 | 20.08 | 6 | b12 | [] | €907,505.33 | €651,548.07 | €1,413,016.00 | 2972069.39
48 | a03Critical Pipes | a03 | Critical Pipes | [] | Unit headloss >10m/km | e01 | 34.06 | 102.81 | 102.79 | €164.68 | 1097.87 | 26.57 | 26.57 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €637,599.17 | €1,148,364.00 | 2693468.49
49 | a03Pump Cost | a03 | Pump Cost | €907,505.33 | Capital Investment | e02 | 34.19 | 102.81 | 102.76 | €165.33 | 1102.19 | 26.68 | 26.68 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €638,051.81 | €1,216,584.00 | 2762141.14
50 | a03Tank Cost | a03 | Tank Cost | €692,488.29 | Capital Investment | e03 | 35.19 | 102.81 | 102.81 | €169.91 | 1132.71 | 27.27 | 27.27 | 1469.6 | 19.91 | 16 | b12 | [] | €907,505.33 | €640,681.32 | €1,287,324.00 | 2835510.64
51 | a03Total Pipe Replacement Cost | a03 | Total Pipe Replacement Cost | €701,174.00 | Capital Investment | e04 | 36.05 | 102.81 | 102.72 | €173.93 | 1159.54 | 28.12 | 28.12 | 1469.6 | 20.1 | 6 | b12 | [] | €907,505.33 | €644,428.06 | €1,417,614.00 | 2969547.39
52 | a03Total Investment Cost | a03 | Total Investment Cost | €2,301,167.61 | Grand Total | e05 | 37.38 | 102.81 | 102.85 | €180.27 | 1201.83 | 29.31 | 29.31 | 1469.6 | 20.08 | 6 | b12 | [] | €907,505.33 | €649,678.42 | €1,449,198.00 | 3006381.75
53 | ------ | --- | --- | --- | --- | e06 | 35.02 | 102.81 | 102.78 | €169.16 | 1127.75 | 27.4 | 27.4 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €641,230.30 | €1,466,163.00 | 3014898.63
54 | Summaryfor | Summary | for | node: | a04 | e07 | 35.8 | 102.81 | 102.81 | €172.79 | 1151.93 | 27.82 | 27.82 | 1469.6 | 19.97 | 6 | b12 | [] | €907,505.33 | €643,102.56 | €1,496,404.00 | 3047011.89
55 | a04Duty Head | a04 | Duty Head | 43.58 | m | e08 | 36.47 | 102.81 | 102.74 | €175.91 | 1172.75 | 28.48 | 28.48 | 1469.6 | 20.1 | 6 | b12 | [] | €907,505.33 | €646,017.16 | €1,593,189.00 | 3146711.49
56 | a04Duty Flow | a04 | Duty Flow | 102.81 | L/s | f01 | 34.44 | 102.81 | 102.78 | €166.44 | 1109.63 | 26.82 | 26.82 | 1469.6 | 20.1 | 16 | b12 | [] | €907,505.33 | €638,698.18 | €1,423,724.00 | 2969927.51
57 | a04Actual average pumped flow: | a04 | Actual average pumped flow: | 102.78 | L/s
58 | a04Cost: | a04 | Cost: | €210.96 | Europerday
59 | a04Energy: | a04 | Energy: | 1406.39 | kWh/day
60 | a04Tank Elevation | a04 | Tank Elevation | 38.04 | m above sea level
61 | a04Tank height above ground | a04 | Tank height above ground | 38.04 | m above nearest node
62 | a04Tank volume | a04 | Tank volume | 1469.6 | m3
63 | a04Minimum Pressure | a04 | Minimum Pressure | 20.09 | mwc
64 | a04Critical Hour | a04 | Critical Hour | 6 | hrs
65 | a04Critical Node | a04 | Critical Node | e05 | Node
66 | a04Critical Pipes | a04 | Critical Pipes | [] | Unit headloss >10m/km
67 | a04Pump Cost | a04 | Pump Cost | €907,505.33 | Capital Investment
68 | a04Tank Cost | a04 | Tank Cost | €688,136.32 | Capital Investment
69 | a04Total Pipe Replacement Cost | a04 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
70 | a04Total Investment Cost | a04 | Total Investment Cost | €2,121,675.65 | Grand Total
71 | ------ | --- | --- | --- | ---
72 | Summaryfor | Summary | for | node: | a05
73 | a05Duty Head | a05 | Duty Head | 43.62 | m
74 | a05Duty Flow | a05 | Duty Flow | 102.81 | L/s
75 | a05Actual average pumped flow: | a05 | Actual average pumped flow: | 102.75 | L/s
76 | a05Cost: | a05 | Cost: | €211.17 | Europerday
77 | a05Energy: | a05 | Energy: | 1407.77 | kWh/day
78 | a05Tank Elevation | a05 | Tank Elevation | 38.21 | m above sea level
79 | a05Tank height above ground | a05 | Tank height above ground | 38.21 | m above nearest node
80 | a05Tank volume | a05 | Tank volume | 1469.6 | m3
81 | a05Minimum Pressure | a05 | Minimum Pressure | 20.09 | mwc
82 | a05Critical Hour | a05 | Critical Hour | 6 | hrs
83 | a05Critical Node | a05 | Critical Node | e05 | Node
84 | a05Critical Pipes | a05 | Critical Pipes | [] | Unit headloss >10m/km
85 | a05Pump Cost | a05 | Pump Cost | €907,505.33 | Capital Investment
86 | a05Tank Cost | a05 | Tank Cost | €688,891.78 | Capital Investment
87 | a05Total Pipe Replacement Cost | a05 | Total Pipe Replacement Cost | €695,279.00 | Capital Investment
88 | a05Total Investment Cost | a05 | Total Investment Cost | €2,291,676.11 | Grand Total
89 | ------ | --- | --- | --- | ---
90 | Summaryfor | Summary | for | node: | a06
91 | a06Duty Head | a06 | Duty Head | 43.12 | m
92 | a06Duty Flow | a06 | Duty Flow | 102.81 | L/s
93 | a06Actual average pumped flow: | a06 | Actual average pumped flow: | 102.78 | L/s
94 | a06Cost: | a06 | Cost: | €208.71 | Europerday
95 | a06Energy: | a06 | Energy: | 1391.42 | kWh/day
96 | a06Tank Elevation | a06 | Tank Elevation | 37.33 | m above sea level
97 | a06Tank height above ground | a06 | Tank height above ground | 37.33 | m above nearest node
98 | a06Tank volume | a06 | Tank volume | 1469.6 | m3
99 | a06Minimum Pressure | a06 | Minimum Pressure | 20.09 | mwc
100 | a06Critical Hour | a06 | Critical Hour | 6 | hrs
101 | a06Critical Node | a06 | Critical Node | e05 | Node
102 | a06Critical Pipes | a06 | Critical Pipes | [] | Unit headloss >10m/km
103 | a06Pump Cost | a06 | Pump Cost | €907,505.33 | Capital Investment
104 | a06Tank Cost | a06 | Tank Cost | €685,018.03 | Capital Investment
105 | a06Total Pipe Replacement Cost | a06 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
106 | a06Total Investment Cost | a06 | Total Investment Cost | €2,118,557.36 | Grand Total
107 | ------ | --- | --- | --- | ---
108 | Summaryfor | Summary | for | node: | a07
109 | a07Duty Head | a07 | Duty Head | 42.82 | m
110 | a07Duty Flow | a07 | Duty Flow | 102.81 | L/s
111 | a07Actual average pumped flow: | a07 | Actual average pumped flow: | 102.78 | L/s
112 | a07Cost: | a07 | Cost: | €207.26 | Europerday
113 | a07Energy: | a07 | Energy: | 1381.75 | kWh/day
114 | a07Tank Elevation | a07 | Tank Elevation | 36.87 | m above sea level
115 | a07Tank height above ground | a07 | Tank height above ground | 36.87 | m above nearest node
116 | a07Tank volume | a07 | Tank volume | 1469.6 | m3
117 | a07Minimum Pressure | a07 | Minimum Pressure | 20.09 | mwc
118 | a07Critical Hour | a07 | Critical Hour | 6 | hrs
119 | a07Critical Node | a07 | Critical Node | e05 | Node
120 | a07Critical Pipes | a07 | Critical Pipes | [] | Unit headloss >10m/km
121 | a07Pump Cost | a07 | Pump Cost | €907,505.33 | Capital Investment
122 | a07Tank Cost | a07 | Tank Cost | €682,991.43 | Capital Investment
123 | a07Total Pipe Replacement Cost | a07 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
124 | a07Total Investment Cost | a07 | Total Investment Cost | €2,116,530.76 | Grand Total
125 | ------ | --- | --- | --- | ---
126 | Summaryfor | Summary | for | node: | a08
127 | a08Duty Head | a08 | Duty Head | 42.74 | m
128 | a08Duty Flow | a08 | Duty Flow | 102.81 | L/s
129 | a08Actual average pumped flow: | a08 | Actual average pumped flow: | 102.76 | L/s
130 | a08Cost: | a08 | Cost: | €206.89 | Europerday
131 | a08Energy: | a08 | Energy: | 1379.28 | kWh/day
132 | a08Tank Elevation | a08 | Tank Elevation | 36.77 | m above sea level
133 | a08Tank height above ground | a08 | Tank height above ground | 36.77 | m above nearest node
134 | a08Tank volume | a08 | Tank volume | 1469.6 | m3
135 | a08Minimum Pressure | a08 | Minimum Pressure | 20.09 | mwc
136 | a08Critical Hour | a08 | Critical Hour | 6 | hrs
137 | a08Critical Node | a08 | Critical Node | e05 | Node
138 | a08Critical Pipes | a08 | Critical Pipes | [] | Unit headloss >10m/km
139 | a08Pump Cost | a08 | Pump Cost | €907,505.33 | Capital Investment
140 | a08Tank Cost | a08 | Tank Cost | €682,568.77 | Capital Investment
141 | a08Total Pipe Replacement Cost | a08 | Total Pipe Replacement Cost | €790,869.00 | Capital Investment
142 | a08Total Investment Cost | a08 | Total Investment Cost | €2,380,943.10 | Grand Total
143 | ------ | --- | --- | --- | ---
144 | Summaryfor | Summary | for | node: | a09
145 | a09Duty Head | a09 | Duty Head | 43 | m
146 | a09Duty Flow | a09 | Duty Flow | 102.81 | L/s
147 | a09Actual average pumped flow: | a09 | Actual average pumped flow: | 102.77 | L/s
148 | a09Cost: | a09 | Cost: | €208.03 | Europerday
149 | a09Energy: | a09 | Energy: | 1386.87 | kWh/day
150 | a09Tank Elevation | a09 | Tank Elevation | 36.87 | m above sea level
151 | a09Tank height above ground | a09 | Tank height above ground | 36.87 | m above nearest node
152 | a09Tank volume | a09 | Tank volume | 1469.6 | m3
153 | a09Minimum Pressure | a09 | Minimum Pressure | 20.1 | mwc
154 | a09Critical Hour | a09 | Critical Hour | 6 | hrs
155 | a09Critical Node | a09 | Critical Node | e05 | Node
156 | a09Critical Pipes | a09 | Critical Pipes | [] | Unit headloss >10m/km
157 | a09Pump Cost | a09 | Pump Cost | €907,505.33 | Capital Investment
158 | a09Tank Cost | a09 | Tank Cost | €682,981.52 | Capital Investment
159 | a09Total Pipe Replacement Cost | a09 | Total Pipe Replacement Cost | €833,700.00 | Capital Investment
160 | a09Total Investment Cost | a09 | Total Investment Cost | €2,424,186.85 | Grand Total
161 | ------ | --- | --- | --- | ---
162 | Summaryfor | Summary | for | node: | a10
163 | a10Duty Head | a10 | Duty Head | 42.8 | m
164 | a10Duty Flow | a10 | Duty Flow | 102.81 | L/s
165 | a10Actual average pumped flow: | a10 | Actual average pumped flow: | 102.8 | L/s
166 | a10Cost: | a10 | Cost: | €207.06 | Europerday
167 | a10Energy: | a10 | Energy: | 1380.41 | kWh/day
168 | a10Tank Elevation | a10 | Tank Elevation | 36.76 | m above sea level
169 | a10Tank height above ground | a10 | Tank height above ground | 36.76 | m above nearest node
170 | a10Tank volume | a10 | Tank volume | 1469.6 | m3
171 | a10Minimum Pressure | a10 | Minimum Pressure | 20.1 | mwc
172 | a10Critical Hour | a10 | Critical Hour | 6 | hrs
173 | a10Critical Node | a10 | Critical Node | e05 | Node
174 | a10Critical Pipes | a10 | Critical Pipes | [] | Unit headloss >10m/km
175 | a10Pump Cost | a10 | Pump Cost | €907,505.33 | Capital Investment
176 | a10Tank Cost | a10 | Tank Cost | €682,504.44 | Capital Investment
177 | a10Total Pipe Replacement Cost | a10 | Total Pipe Replacement Cost | €890,584.00 | Capital Investment
178 | a10Total Investment Cost | a10 | Total Investment Cost | €2,480,593.77 | Grand Total
179 | ------ | --- | --- | --- | ---
180 | Summaryfor | Summary | for | node: | a11
181 | a11Duty Head | a11 | Duty Head | 43.6 | m
182 | a11Duty Flow | a11 | Duty Flow | 102.81 | L/s
183 | a11Actual average pumped flow: | a11 | Actual average pumped flow: | 102.73 | L/s
184 | a11Cost: | a11 | Cost: | €210.96 | Europerday
185 | a11Energy: | a11 | Energy: | 1406.39 | kWh/day
186 | a11Tank Elevation | a11 | Tank Elevation | 37.5 | m above sea level
187 | a11Tank height above ground | a11 | Tank height above ground | 37.5 | m above nearest node
188 | a11Tank volume | a11 | Tank volume | 1469.6 | m3
189 | a11Minimum Pressure | a11 | Minimum Pressure | 20.1 | mwc
190 | a11Critical Hour | a11 | Critical Hour | 6 | hrs
191 | a11Critical Node | a11 | Critical Node | e05 | Node
192 | a11Critical Pipes | a11 | Critical Pipes | [] | Unit headloss >10m/km
193 | a11Pump Cost | a11 | Pump Cost | €907,505.33 | Capital Investment
194 | a11Tank Cost | a11 | Tank Cost | €685,759.83 | Capital Investment
195 | a11Total Pipe Replacement Cost | a11 | Total Pipe Replacement Cost | €901,659.00 | Capital Investment
196 | a11Total Investment Cost | a11 | Total Investment Cost | €2,494,924.16 | Grand Total
197 | ------ | --- | --- | --- | ---
198 | Summaryfor | Summary | for | node: | a12
199 | a12Duty Head | a12 | Duty Head | 43.96 | m
200 | a12Duty Flow | a12 | Duty Flow | 102.81 | L/s
201 | a12Actual average pumped flow: | a12 | Actual average pumped flow: | 102.74 | L/s
202 | a12Cost: | a12 | Cost: | €212.71 | Europerday
203 | a12Energy: | a12 | Energy: | 1418.09 | kWh/day
204 | a12Tank Elevation | a12 | Tank Elevation | 37.94 | m above sea level
205 | a12Tank height above ground | a12 | Tank height above ground | 37.94 | m above nearest node
206 | a12Tank volume | a12 | Tank volume | 1469.6 | m3
207 | a12Minimum Pressure | a12 | Minimum Pressure | 20.09 | mwc
208 | a12Critical Hour | a12 | Critical Hour | 6 | hrs
209 | a12Critical Node | a12 | Critical Node | e05 | Node
210 | a12Critical Pipes | a12 | Critical Pipes | [] | Unit headloss >10m/km
211 | a12Pump Cost | a12 | Pump Cost | €907,505.33 | Capital Investment
212 | a12Tank Cost | a12 | Tank Cost | €687,727.54 | Capital Investment
213 | a12Total Pipe Replacement Cost | a12 | Total Pipe Replacement Cost | €942,969.00 | Capital Investment
214 | a12Total Investment Cost | a12 | Total Investment Cost | €2,538,201.87 | Grand Total
215 | ------ | --- | --- | --- | ---
216 | Summaryfor | Summary | for | node: | a13
217 | a13Duty Head | a13 | Duty Head | 44.2 | m
218 | a13Duty Flow | a13 | Duty Flow | 102.81 | L/s
219 | a13Actual average pumped flow: | a13 | Actual average pumped flow: | 102.81 | L/s
220 | a13Cost: | a13 | Cost: | €213.77 | Europerday
221 | a13Energy: | a13 | Energy: | 1425.13 | kWh/day
222 | a13Tank Elevation | a13 | Tank Elevation | 38.12 | m above sea level
223 | a13Tank height above ground | a13 | Tank height above ground | 38.12 | m above nearest node
224 | a13Tank volume | a13 | Tank volume | 1469.6 | m3
225 | a13Minimum Pressure | a13 | Minimum Pressure | 20.01 | mwc
226 | a13Critical Hour | a13 | Critical Hour | 6 | hrs
227 | a13Critical Node | a13 | Critical Node | e05 | Node
228 | a13Critical Pipes | a13 | Critical Pipes | [] | Unit headloss >10m/km
229 | a13Pump Cost | a13 | Pump Cost | €907,505.33 | Capital Investment
230 | a13Tank Cost | a13 | Tank Cost | €688,490.89 | Capital Investment
231 | a13Total Pipe Replacement Cost | a13 | Total Pipe Replacement Cost | €1,002,279.00 | Capital Investment
232 | a13Total Investment Cost | a13 | Total Investment Cost | €2,598,275.21 | Grand Total
233 | ------ | --- | --- | --- | ---
234 | Summaryfor | Summary | for | node: | a14
235 | a14Duty Head | a14 | Duty Head | 41.99 | m
236 | a14Duty Flow | a14 | Duty Flow | 102.81 | L/s
237 | a14Actual average pumped flow: | a14 | Actual average pumped flow: | 102.81 | L/s
238 | a14Cost: | a14 | Cost: | €203.27 | Europerday
239 | a14Energy: | a14 | Energy: | 1355.12 | kWh/day
240 | a14Tank Elevation | a14 | Tank Elevation | 35.6 | m above sea level
241 | a14Tank height above ground | a14 | Tank height above ground | 35.6 | m above nearest node
242 | a14Tank volume | a14 | Tank volume | 1469.6 | m3
243 | a14Minimum Pressure | a14 | Minimum Pressure | 20.04 | mwc
244 | a14Critical Hour | a14 | Critical Hour | 6 | hrs
245 | a14Critical Node | a14 | Critical Node | e05 | Node
246 | a14Critical Pipes | a14 | Critical Pipes | [] | Unit headloss >10m/km
247 | a14Pump Cost | a14 | Pump Cost | €907,505.33 | Capital Investment
248 | a14Tank Cost | a14 | Tank Cost | €677,414.25 | Capital Investment
249 | a14Total Pipe Replacement Cost | a14 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
250 | a14Total Investment Cost | a14 | Total Investment Cost | €2,110,953.58 | Grand Total
251 | ------ | --- | --- | --- | ---
252 | Summaryfor | Summary | for | node: | a15
253 | a15Duty Head | a15 | Duty Head | 42.78 | m
254 | a15Duty Flow | a15 | Duty Flow | 102.81 | L/s
255 | a15Actual average pumped flow: | a15 | Actual average pumped flow: | 102.73 | L/s
256 | a15Cost: | a15 | Cost: | €207.06 | Europerday
257 | a15Energy: | a15 | Energy: | 1380.4 | kWh/day
258 | a15Tank Elevation | a15 | Tank Elevation | 36.55 | m above sea level
259 | a15Tank height above ground | a15 | Tank height above ground | 36.55 | m above nearest node
260 | a15Tank volume | a15 | Tank volume | 1469.6 | m3
261 | a15Minimum Pressure | a15 | Minimum Pressure | 20.09 | mwc
262 | a15Critical Hour | a15 | Critical Hour | 6 | hrs
263 | a15Critical Node | a15 | Critical Node | e05 | Node
264 | a15Critical Pipes | a15 | Critical Pipes | [] | Unit headloss >10m/km
265 | a15Pump Cost | a15 | Pump Cost | €907,505.33 | Capital Investment
266 | a15Tank Cost | a15 | Tank Cost | €681,594.94 | Capital Investment
267 | a15Total Pipe Replacement Cost | a15 | Total Pipe Replacement Cost | €813,504.00 | Capital Investment
268 | a15Total Investment Cost | a15 | Total Investment Cost | €2,402,604.27 | Grand Total
269 | ------ | --- | --- | --- | ---
270 | Summaryfor | Summary | for | node: | a16
271 | a16Duty Head | a16 | Duty Head | 41.79 | m
272 | a16Duty Flow | a16 | Duty Flow | 102.81 | L/s
273 | a16Actual average pumped flow: | a16 | Actual average pumped flow: | 102.78 | L/s
274 | a16Cost: | a16 | Cost: | €202.26 | Europerday
275 | a16Energy: | a16 | Energy: | 1348.42 | kWh/day
276 | a16Tank Elevation | a16 | Tank Elevation | 35.27 | m above sea level
277 | a16Tank height above ground | a16 | Tank height above ground | 35.27 | m above nearest node
278 | a16Tank volume | a16 | Tank volume | 1469.6 | m3
279 | a16Minimum Pressure | a16 | Minimum Pressure | 20.09 | mwc
280 | a16Critical Hour | a16 | Critical Hour | 6 | hrs
281 | a16Critical Node | a16 | Critical Node | e05 | Node
282 | a16Critical Pipes | a16 | Critical Pipes | [] | Unit headloss >10m/km
283 | a16Pump Cost | a16 | Pump Cost | €907,505.33 | Capital Investment
284 | a16Tank Cost | a16 | Tank Cost | €675,938.21 | Capital Investment
285 | a16Total Pipe Replacement Cost | a16 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
286 | a16Total Investment Cost | a16 | Total Investment Cost | €2,109,477.54 | Grand Total
287 | ------ | --- | --- | --- | ---
288 | Summaryfor | Summary | for | node: | a17
289 | a17Duty Head | a17 | Duty Head | 41.09 | m
290 | a17Duty Flow | a17 | Duty Flow | 102.81 | L/s
291 | a17Actual average pumped flow: | a17 | Actual average pumped flow: | 102.75 | L/s
292 | a17Cost: | a17 | Cost: | €198.90 | Europerday
293 | a17Energy: | a17 | Energy: | 1325.99 | kWh/day
294 | a17Tank Elevation | a17 | Tank Elevation | 34.5 | m above sea level
295 | a17Tank height above ground | a17 | Tank height above ground | 34.5 | m above nearest node
296 | a17Tank volume | a17 | Tank volume | 1469.6 | m3
297 | a17Minimum Pressure | a17 | Minimum Pressure | 20.09 | mwc
298 | a17Critical Hour | a17 | Critical Hour | 6 | hrs
299 | a17Critical Node | a17 | Critical Node | e05 | Node
300 | a17Critical Pipes | a17 | Critical Pipes | [] | Unit headloss >10m/km
301 | a17Pump Cost | a17 | Pump Cost | €907,505.33 | Capital Investment
302 | a17Tank Cost | a17 | Tank Cost | €672,548.31 | Capital Investment
303 | a17Total Pipe Replacement Cost | a17 | Total Pipe Replacement Cost | €695,444.00 | Capital Investment
304 | a17Total Investment Cost | a17 | Total Investment Cost | €2,275,497.63 | Grand Total
305 | ------ | --- | --- | --- | ---
306 | Summaryfor | Summary | for | node: | a18
307 | a18Duty Head | a18 | Duty Head | 41.73 | m
308 | a18Duty Flow | a18 | Duty Flow | 102.81 | L/s
309 | a18Actual average pumped flow: | a18 | Actual average pumped flow: | 102.81 | L/s
310 | a18Cost: | a18 | Cost: | €201.85 | Europerday
311 | a18Energy: | a18 | Energy: | 1345.67 | kWh/day
312 | a18Tank Elevation | a18 | Tank Elevation | 35 | m above sea level
313 | a18Tank height above ground | a18 | Tank height above ground | 35 | m above nearest node
314 | a18Tank volume | a18 | Tank volume | 1469.6 | m3
315 | a18Minimum Pressure | a18 | Minimum Pressure | 20.08 | mwc
316 | a18Critical Hour | a18 | Critical Hour | 6 | hrs
317 | a18Critical Node | a18 | Critical Node | e05 | Node
318 | a18Critical Pipes | a18 | Critical Pipes | [] | Unit headloss >10m/km
319 | a18Pump Cost | a18 | Pump Cost | €907,505.33 | Capital Investment
320 | a18Tank Cost | a18 | Tank Cost | €674,742.30 | Capital Investment
321 | a18Total Pipe Replacement Cost | a18 | Total Pipe Replacement Cost | €730,754.00 | Capital Investment
322 | a18Total Investment Cost | a18 | Total Investment Cost | €2,313,001.63 | Grand Total
323 | ------ | --- | --- | --- | ---
324 | Summaryfor | Summary | for | node: | a19
325 | a19Duty Head | a19 | Duty Head | 39.54 | m
326 | a19Duty Flow | a19 | Duty Flow | 102.81 | L/s
327 | a19Actual average pumped flow: | a19 | Actual average pumped flow: | 102.78 | L/s
328 | a19Cost: | a19 | Cost: | €191.32 | Europerday
329 | a19Energy: | a19 | Energy: | 1275.49 | kWh/day
330 | a19Tank Elevation | a19 | Tank Elevation | 32.75 | m above sea level
331 | a19Tank height above ground | a19 | Tank height above ground | 32.75 | m above nearest node
332 | a19Tank volume | a19 | Tank volume | 1469.6 | m3
333 | a19Minimum Pressure | a19 | Minimum Pressure | 20.1 | mwc
334 | a19Critical Hour | a19 | Critical Hour | 16 | hrs
335 | a19Critical Node | a19 | Critical Node | e05 | Node
336 | a19Critical Pipes | a19 | Critical Pipes | [] | Unit headloss >10m/km
337 | a19Pump Cost | a19 | Pump Cost | €907,505.33 | Capital Investment
338 | a19Tank Cost | a19 | Tank Cost | €664,811.36 | Capital Investment
339 | a19Total Pipe Replacement Cost | a19 | Total Pipe Replacement Cost | €628,994.00 | Capital Investment
340 | a19Total Investment Cost | a19 | Total Investment Cost | €2,201,310.69 | Grand Total
341 | ------ | --- | --- | --- | ---
342 | Summaryfor | Summary | for | node: | a20
343 | a20Duty Head | a20 | Duty Head | 39.76 | m
344 | a20Duty Flow | a20 | Duty Flow | 102.81 | L/s
345 | a20Actual average pumped flow: | a20 | Actual average pumped flow: | 102.77 | L/s
346 | a20Cost: | a20 | Cost: | €192.40 | Europerday
347 | a20Energy: | a20 | Energy: | 1282.69 | kWh/day
348 | a20Tank Elevation | a20 | Tank Elevation | 33.08 | m above sea level
349 | a20Tank height above ground | a20 | Tank height above ground | 33.08 | m above nearest node
350 | a20Tank volume | a20 | Tank volume | 1469.6 | m3
351 | a20Minimum Pressure | a20 | Minimum Pressure | 20.09 | mwc
352 | a20Critical Hour | a20 | Critical Hour | 16 | hrs
353 | a20Critical Node | a20 | Critical Node | e05 | Node
354 | a20Critical Pipes | a20 | Critical Pipes | [] | Unit headloss >10m/km
355 | a20Pump Cost | a20 | Pump Cost | €907,505.33 | Capital Investment
356 | a20Tank Cost | a20 | Tank Cost | €666,282.10 | Capital Investment
357 | a20Total Pipe Replacement Cost | a20 | Total Pipe Replacement Cost | €823,739.00 | Capital Investment
358 | a20Total Investment Cost | a20 | Total Investment Cost | €2,397,526.43 | Grand Total
359 | ------ | --- | --- | --- | ---
360 | Summaryfor | Summary | for | node: | a21
361 | a21Duty Head | a21 | Duty Head | 40.09 | m
362 | a21Duty Flow | a21 | Duty Flow | 102.81 | L/s
363 | a21Actual average pumped flow: | a21 | Actual average pumped flow: | 102.74 | L/s
364 | a21Cost: | a21 | Cost: | €194.02 | Europerday
365 | a21Energy: | a21 | Energy: | 1293.46 | kWh/day
366 | a21Tank Elevation | a21 | Tank Elevation | 33.43 | m above sea level
367 | a21Tank height above ground | a21 | Tank height above ground | 33.43 | m above nearest node
368 | a21Tank volume | a21 | Tank volume | 1469.6 | m3
369 | a21Minimum Pressure | a21 | Minimum Pressure | 20.09 | mwc
370 | a21Critical Hour | a21 | Critical Hour | 6 | hrs
371 | a21Critical Node | a21 | Critical Node | e05 | Node
372 | a21Critical Pipes | a21 | Critical Pipes | [] | Unit headloss >10m/km
373 | a21Pump Cost | a21 | Pump Cost | €907,505.33 | Capital Investment
374 | a21Tank Cost | a21 | Tank Cost | €667,817.26 | Capital Investment
375 | a21Total Pipe Replacement Cost | a21 | Total Pipe Replacement Cost | €892,709.00 | Capital Investment
376 | a21Total Investment Cost | a21 | Total Investment Cost | €2,468,031.59 | Grand Total
377 | ------ | --- | --- | --- | ---
378 | Summaryfor | Summary | for | node: | b01
379 | b01Duty Head | b01 | Duty Head | 37.16 | m
380 | b01Duty Flow | b01 | Duty Flow | 102.81 | L/s
381 | b01Actual average pumped flow: | b01 | Actual average pumped flow: | 102.75 | L/s
382 | b01Cost: | b01 | Cost: | €179.83 | Europerday
383 | b01Energy: | b01 | Energy: | 1198.84 | kWh/day
384 | b01Tank Elevation | b01 | Tank Elevation | 30.1 | m above sea level
385 | b01Tank height above ground | b01 | Tank height above ground | 30.1 | m above nearest node
386 | b01Tank volume | b01 | Tank volume | 1469.6 | m3
387 | b01Minimum Pressure | b01 | Minimum Pressure | 20.09 | mwc
388 | b01Critical Hour | b01 | Critical Hour | 16 | hrs
389 | b01Critical Node | b01 | Critical Node | e05 | Node
390 | b01Critical Pipes | b01 | Critical Pipes | [] | Unit headloss >10m/km
391 | b01Pump Cost | b01 | Pump Cost | €907,505.33 | Capital Investment
392 | b01Tank Cost | b01 | Tank Cost | €653,165.04 | Capital Investment
393 | b01Total Pipe Replacement Cost | b01 | Total Pipe Replacement Cost | €762,914.00 | Capital Investment
394 | b01Total Investment Cost | b01 | Total Investment Cost | €2,323,584.37 | Grand Total
395 | ------ | --- | --- | --- | ---
396 | Summaryfor | Summary | for | node: | b02
397 | b02Duty Head | b02 | Duty Head | 37.29 | m
398 | b02Duty Flow | b02 | Duty Flow | 102.81 | L/s
399 | b02Actual average pumped flow: | b02 | Actual average pumped flow: | 102.72 | L/s
400 | b02Cost: | b02 | Cost: | €180.42 | Europerday
401 | b02Energy: | b02 | Energy: | 1202.83 | kWh/day
402 | b02Tank Elevation | b02 | Tank Elevation | 30.17 | m above sea level
403 | b02Tank height above ground | b02 | Tank height above ground | 30.17 | m above nearest node
404 | b02Tank volume | b02 | Tank volume | 1469.6 | m3
405 | b02Minimum Pressure | b02 | Minimum Pressure | 20.1 | mwc
406 | b02Critical Hour | b02 | Critical Hour | 16 | hrs
407 | b02Critical Node | b02 | Critical Node | e05 | Node
408 | b02Critical Pipes | b02 | Critical Pipes | [] | Unit headloss >10m/km
409 | b02Pump Cost | b02 | Pump Cost | €907,505.33 | Capital Investment
410 | b02Tank Cost | b02 | Tank Cost | €653,460.44 | Capital Investment
411 | b02Total Pipe Replacement Cost | b02 | Total Pipe Replacement Cost | €901,514.00 | Capital Investment
412 | b02Total Investment Cost | b02 | Total Investment Cost | €2,462,479.77 | Grand Total
413 | ------ | --- | --- | --- | ---
414 | Summaryfor | Summary | for | node: | b03
415 | b03Duty Head | b03 | Duty Head | 37.41 | m
416 | b03Duty Flow | b03 | Duty Flow | 102.81 | L/s
417 | b03Actual average pumped flow: | b03 | Actual average pumped flow: | 102.81 | L/s
418 | b03Cost: | b03 | Cost: | €180.97 | Europerday
419 | b03Energy: | b03 | Energy: | 1206.44 | kWh/day
420 | b03Tank Elevation | b03 | Tank Elevation | 30.17 | m above sea level
421 | b03Tank height above ground | b03 | Tank height above ground | 30.17 | m above nearest node
422 | b03Tank volume | b03 | Tank volume | 1469.6 | m3
423 | b03Minimum Pressure | b03 | Minimum Pressure | 20.09 | mwc
424 | b03Critical Hour | b03 | Critical Hour | 16 | hrs
425 | b03Critical Node | b03 | Critical Node | e05 | Node
426 | b03Critical Pipes | b03 | Critical Pipes | [] | Unit headloss >10m/km
427 | b03Pump Cost | b03 | Pump Cost | €907,505.33 | Capital Investment
428 | b03Tank Cost | b03 | Tank Cost | €653,475.24 | Capital Investment
429 | b03Total Pipe Replacement Cost | b03 | Total Pipe Replacement Cost | €990,794.00 | Capital Investment
430 | b03Total Investment Cost | b03 | Total Investment Cost | €2,551,774.57 | Grand Total
431 | ------ | --- | --- | --- | ---
432 | Summaryfor | Summary | for | node: | b04
433 | b04Duty Head | b04 | Duty Head | 37.55 | m
434 | b04Duty Flow | b04 | Duty Flow | 102.81 | L/s
435 | b04Actual average pumped flow: | b04 | Actual average pumped flow: | 102.76 | L/s
436 | b04Cost: | b04 | Cost: | €181.61 | Europerday
437 | b04Energy: | b04 | Energy: | 1210.74 | kWh/day
438 | b04Tank Elevation | b04 | Tank Elevation | 30.31 | m above sea level
439 | b04Tank height above ground | b04 | Tank height above ground | 30.31 | m above nearest node
440 | b04Tank volume | b04 | Tank volume | 1469.6 | m3
441 | b04Minimum Pressure | b04 | Minimum Pressure | 20.1 | mwc
442 | b04Critical Hour | b04 | Critical Hour | 16 | hrs
443 | b04Critical Node | b04 | Critical Node | e05 | Node
444 | b04Critical Pipes | b04 | Critical Pipes | [] | Unit headloss >10m/km
445 | b04Pump Cost | b04 | Pump Cost | €907,505.33 | Capital Investment
446 | b04Tank Cost | b04 | Tank Cost | €654,079.77 | Capital Investment
447 | b04Total Pipe Replacement Cost | b04 | Total Pipe Replacement Cost | €1,123,368.00 | Capital Investment
448 | b04Total Investment Cost | b04 | Total Investment Cost | €2,684,953.10 | Grand Total
449 | ------ | --- | --- | --- | ---
450 | Summaryfor | Summary | for | node: | b05
451 | b05Duty Head | b05 | Duty Head | 38.37 | m
452 | b05Duty Flow | b05 | Duty Flow | 102.81 | L/s
453 | b05Actual average pumped flow: | b05 | Actual average pumped flow: | 102.81 | L/s
454 | b05Cost: | b05 | Cost: | €185.41 | Europerday
455 | b05Energy: | b05 | Energy: | 1236.1 | kWh/day
456 | b05Tank Elevation | b05 | Tank Elevation | 30.92 | m above sea level
457 | b05Tank height above ground | b05 | Tank height above ground | 30.92 | m above nearest node
458 | b05Tank volume | b05 | Tank volume | 1469.6 | m3
459 | b05Minimum Pressure | b05 | Minimum Pressure | 19.95 | mwc
460 | b05Critical Hour | b05 | Critical Hour | 16 | hrs
461 | b05Critical Node | b05 | Critical Node | e05 | Node
462 | b05Critical Pipes | b05 | Critical Pipes | [] | Unit headloss >10m/km
463 | b05Pump Cost | b05 | Pump Cost | €907,505.33 | Capital Investment
464 | b05Tank Cost | b05 | Tank Cost | €656,758.23 | Capital Investment
465 | b05Total Pipe Replacement Cost | b05 | Total Pipe Replacement Cost | €1,230,660.00 | Capital Investment
466 | b05Total Investment Cost | b05 | Total Investment Cost | €2,794,923.56 | Grand Total
467 | ------ | --- | --- | --- | ---
468 | Summaryfor | Summary | for | node: | b06
469 | b06Duty Head | b06 | Duty Head | 37.62 | m
470 | b06Duty Flow | b06 | Duty Flow | 102.81 | L/s
471 | b06Actual average pumped flow: | b06 | Actual average pumped flow: | 102.78 | L/s
472 | b06Cost: | b06 | Cost: | €181.93 | Europerday
473 | b06Energy: | b06 | Energy: | 1212.84 | kWh/day
474 | b06Tank Elevation | b06 | Tank Elevation | 30.36 | m above sea level
475 | b06Tank height above ground | b06 | Tank height above ground | 30.36 | m above nearest node
476 | b06Tank volume | b06 | Tank volume | 1469.6 | m3
477 | b06Minimum Pressure | b06 | Minimum Pressure | 20.1 | mwc
478 | b06Critical Hour | b06 | Critical Hour | 16 | hrs
479 | b06Critical Node | b06 | Critical Node | e05 | Node
480 | b06Critical Pipes | b06 | Critical Pipes | [] | Unit headloss >10m/km
481 | b06Pump Cost | b06 | Pump Cost | €907,505.33 | Capital Investment
482 | b06Tank Cost | b06 | Tank Cost | €654,282.57 | Capital Investment
483 | b06Total Pipe Replacement Cost | b06 | Total Pipe Replacement Cost | €1,175,820.00 | Capital Investment
484 | b06Total Investment Cost | b06 | Total Investment Cost | €2,737,607.89 | Grand Total
485 | ------ | --- | --- | --- | ---
486 | Summaryfor | Summary | for | node: | b07
487 | b07Duty Head | b07 | Duty Head | 38.34 | m
488 | b07Duty Flow | b07 | Duty Flow | 102.81 | L/s
489 | b07Actual average pumped flow: | b07 | Actual average pumped flow: | 102.81 | L/s
490 | b07Cost: | b07 | Cost: | €185.29 | Europerday
491 | b07Energy: | b07 | Energy: | 1235.26 | kWh/day
492 | b07Tank Elevation | b07 | Tank Elevation | 30.94 | m above sea level
493 | b07Tank height above ground | b07 | Tank height above ground | 30.94 | m above nearest node
494 | b07Tank volume | b07 | Tank volume | 1469.6 | m3
495 | b07Minimum Pressure | b07 | Minimum Pressure | 19.99 | mwc
496 | b07Critical Hour | b07 | Critical Hour | 16 | hrs
497 | b07Critical Node | b07 | Critical Node | e05 | Node
498 | b07Critical Pipes | b07 | Critical Pipes | [] | Unit headloss >10m/km
499 | b07Pump Cost | b07 | Pump Cost | €907,505.33 | Capital Investment
500 | b07Tank Cost | b07 | Tank Cost | €656,852.15 | Capital Investment
501 | b07Total Pipe Replacement Cost | b07 | Total Pipe Replacement Cost | €1,195,773.00 | Capital Investment
502 | b07Total Investment Cost | b07 | Total Investment Cost | €2,760,130.47 | Grand Total
503 | ------ | --- | --- | --- | ---
504 | Summaryfor | Summary | for | node: | b08
505 | b08Duty Head | b08 | Duty Head | 38.67 | m
506 | b08Duty Flow | b08 | Duty Flow | 102.81 | L/s
507 | b08Actual average pumped flow: | b08 | Actual average pumped flow: | 102.74 | L/s
508 | b08Cost: | b08 | Cost: | €186.82 | Europerday
509 | b08Energy: | b08 | Energy: | 1245.47 | kWh/day
510 | b08Tank Elevation | b08 | Tank Elevation | 31.25 | m above sea level
511 | b08Tank height above ground | b08 | Tank height above ground | 31.25 | m above nearest node
512 | b08Tank volume | b08 | Tank volume | 1469.6 | m3
513 | b08Minimum Pressure | b08 | Minimum Pressure | 20.1 | mwc
514 | b08Critical Hour | b08 | Critical Hour | 16 | hrs
515 | b08Critical Node | b08 | Critical Node | e05 | Node
516 | b08Critical Pipes | b08 | Critical Pipes | [] | Unit headloss >10m/km
517 | b08Pump Cost | b08 | Pump Cost | €907,505.33 | Capital Investment
518 | b08Tank Cost | b08 | Tank Cost | €658,217.49 | Capital Investment
519 | b08Total Pipe Replacement Cost | b08 | Total Pipe Replacement Cost | €1,321,665.00 | Capital Investment
520 | b08Total Investment Cost | b08 | Total Investment Cost | €2,887,387.82 | Grand Total
521 | ------ | --- | --- | --- | ---
522 | Summaryfor | Summary | for | node: | b09
523 | b09Duty Head | b09 | Duty Head | 37.59 | m
524 | b09Duty Flow | b09 | Duty Flow | 102.81 | L/s
525 | b09Actual average pumped flow: | b09 | Actual average pumped flow: | 102.78 | L/s
526 | b09Cost: | b09 | Cost: | €181.79 | Europerday
527 | b09Energy: | b09 | Energy: | 1211.95 | kWh/day
528 | b09Tank Elevation | b09 | Tank Elevation | 30.34 | m above sea level
529 | b09Tank height above ground | b09 | Tank height above ground | 30.34 | m above nearest node
530 | b09Tank volume | b09 | Tank volume | 1469.6 | m3
531 | b09Minimum Pressure | b09 | Minimum Pressure | 20.1 | mwc
532 | b09Critical Hour | b09 | Critical Hour | 16 | hrs
533 | b09Critical Node | b09 | Critical Node | e05 | Node
534 | b09Critical Pipes | b09 | Critical Pipes | [] | Unit headloss >10m/km
535 | b09Pump Cost | b09 | Pump Cost | €907,505.33 | Capital Investment
536 | b09Tank Cost | b09 | Tank Cost | €654,219.18 | Capital Investment
537 | b09Total Pipe Replacement Cost | b09 | Total Pipe Replacement Cost | €1,175,778.00 | Capital Investment
538 | b09Total Investment Cost | b09 | Total Investment Cost | €2,737,502.51 | Grand Total
539 | ------ | --- | --- | --- | ---
540 | Summaryfor | Summary | for | node: | b10
541 | b10Duty Head | b10 | Duty Head | 38.34 | m
542 | b10Duty Flow | b10 | Duty Flow | 102.81 | L/s
543 | b10Actual average pumped flow: | b10 | Actual average pumped flow: | 102.81 | L/s
544 | b10Cost: | b10 | Cost: | €185.29 | Europerday
545 | b10Energy: | b10 | Energy: | 1235.28 | kWh/day
546 | b10Tank Elevation | b10 | Tank Elevation | 31 | m above sea level
547 | b10Tank height above ground | b10 | Tank height above ground | 31 | m above nearest node
548 | b10Tank volume | b10 | Tank volume | 1469.6 | m3
549 | b10Minimum Pressure | b10 | Minimum Pressure | 19.99 | mwc
550 | b10Critical Hour | b10 | Critical Hour | 16 | hrs
551 | b10Critical Node | b10 | Critical Node | e05 | Node
552 | b10Critical Pipes | b10 | Critical Pipes | [] | Unit headloss >10m/km
553 | b10Pump Cost | b10 | Pump Cost | €907,505.33 | Capital Investment
554 | b10Tank Cost | b10 | Tank Cost | €657,119.84 | Capital Investment
555 | b10Total Pipe Replacement Cost | b10 | Total Pipe Replacement Cost | €1,180,008.00 | Capital Investment
556 | b10Total Investment Cost | b10 | Total Investment Cost | €2,744,633.17 | Grand Total
557 | ------ | --- | --- | --- | ---
558 | Summaryfor | Summary | for | node: | b11
559 | b11Duty Head | b11 | Duty Head | 40.13 | m
560 | b11Duty Flow | b11 | Duty Flow | 102.81 | L/s
561 | b11Actual average pumped flow: | b11 | Actual average pumped flow: | 102.84 | L/s
562 | b11Cost: | b11 | Cost: | €193.64 | Europerday
563 | b11Energy: | b11 | Energy: | 1290.91 | kWh/day
564 | b11Tank Elevation | b11 | Tank Elevation | 32.17 | m above sea level
565 | b11Tank height above ground | b11 | Tank height above ground | 32.17 | m above nearest node
566 | b11Tank volume | b11 | Tank volume | 1469.6 | m3
567 | b11Minimum Pressure | b11 | Minimum Pressure | 20.09 | mwc
568 | b11Critical Hour | b11 | Critical Hour | 6 | hrs
569 | b11Critical Node | b11 | Critical Node | e05 | Node
570 | b11Critical Pipes | b11 | Critical Pipes | [] | Unit headloss >10m/km
571 | b11Pump Cost | b11 | Pump Cost | €907,505.33 | Capital Investment
572 | b11Tank Cost | b11 | Tank Cost | €662,259.66 | Capital Investment
573 | b11Total Pipe Replacement Cost | b11 | Total Pipe Replacement Cost | €1,231,931.00 | Capital Investment
574 | b11Total Investment Cost | b11 | Total Investment Cost | €2,801,695.99 | Grand Total
575 | ------ | --- | --- | --- | ---
576 | Summaryfor | Summary | for | node: | b12
577 | b12Duty Head | b12 | Duty Head | 38.68 | m
578 | b12Duty Flow | b12 | Duty Flow | 102.81 | L/s
579 | b12Actual average pumped flow: | b12 | Actual average pumped flow: | 102.78 | L/s
580 | b12Cost: | b12 | Cost: | €186.88 | Europerday
581 | b12Energy: | b12 | Energy: | 1245.86 | kWh/day
582 | b12Tank Elevation | b12 | Tank Elevation | 31.21 | m above sea level
583 | b12Tank height above ground | b12 | Tank height above ground | 31.21 | m above nearest node
584 | b12Tank volume | b12 | Tank volume | 1469.6 | m3
585 | b12Minimum Pressure | b12 | Minimum Pressure | 20.1 | mwc
586 | b12Critical Hour | b12 | Critical Hour | 16 | hrs
587 | b12Critical Node | b12 | Critical Node | e05 | Node
588 | b12Critical Pipes | b12 | Critical Pipes | [] | Unit headloss >10m/km
589 | b12Pump Cost | b12 | Pump Cost | €907,505.33 | Capital Investment
590 | b12Tank Cost | b12 | Tank Cost | €658,026.79 | Capital Investment
591 | b12Total Pipe Replacement Cost | b12 | Total Pipe Replacement Cost | €1,415,572.00 | Capital Investment
592 | b12Total Investment Cost | b12 | Total Investment Cost | €2,981,104.11 | Grand Total
593 | ------ | --- | --- | --- | ---
594 | Summaryfor | Summary | for | node: | c01
595 | c01Duty Head | c01 | Duty Head | 34 | m
596 | c01Duty Flow | c01 | Duty Flow | 102.81 | L/s
597 | c01Actual average pumped flow: | c01 | Actual average pumped flow: | 102.78 | L/s
598 | c01Cost: | c01 | Cost: | €164.41 | Europerday
599 | c01Energy: | c01 | Energy: | 1096.04 | kWh/day
600 | c01Tank Elevation | c01 | Tank Elevation | 26.57 | m above sea level
601 | c01Tank height above ground | c01 | Tank height above ground | 26.57 | m above nearest node
602 | c01Tank volume | c01 | Tank volume | 1469.6 | m3
603 | c01Minimum Pressure | c01 | Minimum Pressure | 20.1 | mwc
604 | c01Critical Hour | c01 | Critical Hour | 16 | hrs
605 | c01Critical Node | c01 | Critical Node | b12 | Node
606 | c01Critical Pipes | c01 | Critical Pipes | [] | Unit headloss >10m/km
607 | c01Pump Cost | c01 | Pump Cost | €907,505.33 | Capital Investment
608 | c01Tank Cost | c01 | Tank Cost | €637,571.18 | Capital Investment
609 | c01Total Pipe Replacement Cost | c01 | Total Pipe Replacement Cost | €1,049,974.00 | Capital Investment
610 | c01Total Investment Cost | c01 | Total Investment Cost | €2,595,050.51 | Grand Total
611 | ------ | --- | --- | --- | ---
612 | Summaryfor | Summary | for | node: | c02
613 | c02Duty Head | c02 | Duty Head | 34.09 | m
614 | c02Duty Flow | c02 | Duty Flow | 102.81 | L/s
615 | c02Actual average pumped flow: | c02 | Actual average pumped flow: | 102.77 | L/s
616 | c02Cost: | c02 | Cost: | €164.84 | Europerday
617 | c02Energy: | c02 | Energy: | 1098.95 | kWh/day
618 | c02Tank Elevation | c02 | Tank Elevation | 26.65 | m above sea level
619 | c02Tank height above ground | c02 | Tank height above ground | 26.65 | m above nearest node
620 | c02Tank volume | c02 | Tank volume | 1469.6 | m3
621 | c02Minimum Pressure | c02 | Minimum Pressure | 20.1 | mwc
622 | c02Critical Hour | c02 | Critical Hour | 16 | hrs
623 | c02Critical Node | c02 | Critical Node | b12 | Node
624 | c02Critical Pipes | c02 | Critical Pipes | [] | Unit headloss >10m/km
625 | c02Pump Cost | c02 | Pump Cost | €907,505.33 | Capital Investment
626 | c02Tank Cost | c02 | Tank Cost | €637,940.03 | Capital Investment
627 | c02Total Pipe Replacement Cost | c02 | Total Pipe Replacement Cost | €1,198,284.00 | Capital Investment
628 | c02Total Investment Cost | c02 | Total Investment Cost | €2,743,729.36 | Grand Total
629 | ------ | --- | --- | --- | ---
630 | Summaryfor | Summary | for | node: | c03
631 | c03Duty Head | c03 | Duty Head | 34.74 | m
632 | c03Duty Flow | c03 | Duty Flow | 102.81 | L/s
633 | c03Actual average pumped flow: | c03 | Actual average pumped flow: | 102.81 | L/s
634 | c03Cost: | c03 | Cost: | €167.85 | Europerday
635 | c03Energy: | c03 | Energy: | 1119.03 | kWh/day
636 | c03Tank Elevation | c03 | Tank Elevation | 27.16 | m above sea level
637 | c03Tank height above ground | c03 | Tank height above ground | 27.16 | m above nearest node
638 | c03Tank volume | c03 | Tank volume | 1469.6 | m3
639 | c03Minimum Pressure | c03 | Minimum Pressure | 20.01 | mwc
640 | c03Critical Hour | c03 | Critical Hour | 16 | hrs
641 | c03Critical Node | c03 | Critical Node | b12 | Node
642 | c03Critical Pipes | c03 | Critical Pipes | [] | Unit headloss >10m/km
643 | c03Pump Cost | c03 | Pump Cost | €907,505.33 | Capital Investment
644 | c03Tank Cost | c03 | Tank Cost | €640,173.89 | Capital Investment
645 | c03Total Pipe Replacement Cost | c03 | Total Pipe Replacement Cost | €1,269,619.00 | Capital Investment
646 | c03Total Investment Cost | c03 | Total Investment Cost | €2,817,298.21 | Grand Total
647 | ------ | --- | --- | --- | ---
648 | Summaryfor | Summary | for | node: | c04
649 | c04Duty Head | c04 | Duty Head | 34.91 | m
650 | c04Duty Flow | c04 | Duty Flow | 102.81 | L/s
651 | c04Actual average pumped flow: | c04 | Actual average pumped flow: | 102.78 | L/s
652 | c04Cost: | c04 | Cost: | €168.69 | Europerday
653 | c04Energy: | c04 | Energy: | 1124.6 | kWh/day
654 | c04Tank Elevation | c04 | Tank Elevation | 27.33 | m above sea level
655 | c04Tank height above ground | c04 | Tank height above ground | 27.33 | m above nearest node
656 | c04Tank volume | c04 | Tank volume | 1469.6 | m3
657 | c04Minimum Pressure | c04 | Minimum Pressure | 20.1 | mwc
658 | c04Critical Hour | c04 | Critical Hour | 16 | hrs
659 | c04Critical Node | c04 | Critical Node | b12 | Node
660 | c04Critical Pipes | c04 | Critical Pipes | [] | Unit headloss >10m/km
661 | c04Pump Cost | c04 | Pump Cost | €907,505.33 | Capital Investment
662 | c04Tank Cost | c04 | Tank Cost | €640,915.06 | Capital Investment
663 | c04Total Pipe Replacement Cost | c04 | Total Pipe Replacement Cost | €1,332,844.00 | Capital Investment
664 | c04Total Investment Cost | c04 | Total Investment Cost | €2,881,264.38 | Grand Total
665 | ------ | --- | --- | --- | ---
666 | Summaryfor | Summary | for | node: | c05
667 | c05Duty Head | c05 | Duty Head | 34.22 | m
668 | c05Duty Flow | c05 | Duty Flow | 102.81 | L/s
669 | c05Actual average pumped flow: | c05 | Actual average pumped flow: | 102.78 | L/s
670 | c05Cost: | c05 | Cost: | €165.43 | Europerday
671 | c05Energy: | c05 | Energy: | 1102.86 | kWh/day
672 | c05Tank Elevation | c05 | Tank Elevation | 26.67 | m above sea level
673 | c05Tank height above ground | c05 | Tank height above ground | 26.67 | m above nearest node
674 | c05Tank volume | c05 | Tank volume | 1469.6 | m3
675 | c05Minimum Pressure | c05 | Minimum Pressure | 20.1 | mwc
676 | c05Critical Hour | c05 | Critical Hour | 16 | hrs
677 | c05Critical Node | c05 | Critical Node | b12 | Node
678 | c05Critical Pipes | c05 | Critical Pipes | [] | Unit headloss >10m/km
679 | c05Pump Cost | c05 | Pump Cost | €907,505.33 | Capital Investment
680 | c05Tank Cost | c05 | Tank Cost | €638,022.14 | Capital Investment
681 | c05Total Pipe Replacement Cost | c05 | Total Pipe Replacement Cost | €1,296,246.00 | Capital Investment
682 | c05Total Investment Cost | c05 | Total Investment Cost | €2,841,773.47 | Grand Total
683 | ------ | --- | --- | --- | ---
684 | Summaryfor | Summary | for | node: | c06
685 | c06Duty Head | c06 | Duty Head | 35 | m
686 | c06Duty Flow | c06 | Duty Flow | 102.81 | L/s
687 | c06Actual average pumped flow: | c06 | Actual average pumped flow: | 102.81 | L/s
688 | c06Cost: | c06 | Cost: | €169.03 | Europerday
689 | c06Energy: | c06 | Energy: | 1126.89 | kWh/day
690 | c06Tank Elevation | c06 | Tank Elevation | 27.11 | m above sea level
691 | c06Tank height above ground | c06 | Tank height above ground | 27.11 | m above nearest node
692 | c06Tank volume | c06 | Tank volume | 1469.6 | m3
693 | c06Minimum Pressure | c06 | Minimum Pressure | 19.99 | mwc
694 | c06Critical Hour | c06 | Critical Hour | 16 | hrs
695 | c06Critical Node | c06 | Critical Node | b12 | Node
696 | c06Critical Pipes | c06 | Critical Pipes | [] | Unit headloss >10m/km
697 | c06Pump Cost | c06 | Pump Cost | €907,505.33 | Capital Investment
698 | c06Tank Cost | c06 | Tank Cost | €639,955.10 | Capital Investment
699 | c06Total Pipe Replacement Cost | c06 | Total Pipe Replacement Cost | €1,317,184.00 | Capital Investment
700 | c06Total Investment Cost | c06 | Total Investment Cost | €2,864,644.43 | Grand Total
701 | ------ | --- | --- | --- | ---
702 | Summaryfor | Summary | for | node: | c07
703 | c07Duty Head | c07 | Duty Head | 35.38 | m
704 | c07Duty Flow | c07 | Duty Flow | 102.81 | L/s
705 | c07Actual average pumped flow: | c07 | Actual average pumped flow: | 102.77 | L/s
706 | c07Cost: | c07 | Cost: | €170.84 | Europerday
707 | c07Energy: | c07 | Energy: | 1138.92 | kWh/day
708 | c07Tank Elevation | c07 | Tank Elevation | 27.56 | m above sea level
709 | c07Tank height above ground | c07 | Tank height above ground | 27.56 | m above nearest node
710 | c07Tank volume | c07 | Tank volume | 1469.6 | m3
711 | c07Minimum Pressure | c07 | Minimum Pressure | 20.1 | mwc
712 | c07Critical Hour | c07 | Critical Hour | 16 | hrs
713 | c07Critical Node | c07 | Critical Node | b12 | Node
714 | c07Critical Pipes | c07 | Critical Pipes | [] | Unit headloss >10m/km
715 | c07Pump Cost | c07 | Pump Cost | €907,505.33 | Capital Investment
716 | c07Tank Cost | c07 | Tank Cost | €641,962.19 | Capital Investment
717 | c07Total Pipe Replacement Cost | c07 | Total Pipe Replacement Cost | €1,336,354.00 | Capital Investment
718 | c07Total Investment Cost | c07 | Total Investment Cost | €2,885,821.52 | Grand Total
719 | ------ | --- | --- | --- | ---
720 | Summaryfor | Summary | for | node: | d01
721 | d01Duty Head | d01 | Duty Head | 34.22 | m
722 | d01Duty Flow | d01 | Duty Flow | 102.81 | L/s
723 | d01Actual average pumped flow: | d01 | Actual average pumped flow: | 102.78 | L/s
724 | d01Cost: | d01 | Cost: | €165.46 | Europerday
725 | d01Energy: | d01 | Energy: | 1103.05 | kWh/day
726 | d01Tank Elevation | d01 | Tank Elevation | 26.75 | m above sea level
727 | d01Tank height above ground | d01 | Tank height above ground | 26.75 | m above nearest node
728 | d01Tank volume | d01 | Tank volume | 1469.6 | m3
729 | d01Minimum Pressure | d01 | Minimum Pressure | 20.1 | mwc
730 | d01Critical Hour | d01 | Critical Hour | 16 | hrs
731 | d01Critical Node | d01 | Critical Node | b12 | Node
732 | d01Critical Pipes | d01 | Critical Pipes | [] | Unit headloss >10m/km
733 | d01Pump Cost | d01 | Pump Cost | €907,505.33 | Capital Investment
734 | d01Tank Cost | d01 | Tank Cost | €638,392.26 | Capital Investment
735 | d01Total Pipe Replacement Cost | d01 | Total Pipe Replacement Cost | €1,229,074.00 | Capital Investment
736 | d01Total Investment Cost | d01 | Total Investment Cost | €2,774,971.58 | Grand Total
737 | ------ | --- | --- | --- | ---
738 | Summaryfor | Summary | for | node: | d02
739 | d02Duty Head | d02 | Duty Head | 35.79 | m
740 | d02Duty Flow | d02 | Duty Flow | 102.81 | L/s
741 | d02Actual average pumped flow: | d02 | Actual average pumped flow: | 102.84 | L/s
742 | d02Cost: | d02 | Cost: | €172.84 | Europerday
743 | d02Energy: | d02 | Energy: | 1152.27 | kWh/day
744 | d02Tank Elevation | d02 | Tank Elevation | 28.15 | m above sea level
745 | d02Tank height above ground | d02 | Tank height above ground | 28.15 | m above nearest node
746 | d02Tank volume | d02 | Tank volume | 1469.6 | m3
747 | d02Minimum Pressure | d02 | Minimum Pressure | 20.09 | mwc
748 | d02Critical Hour | d02 | Critical Hour | 6 | hrs
749 | d02Critical Node | d02 | Critical Node | b12 | Node
750 | d02Critical Pipes | d02 | Critical Pipes | [] | Unit headloss >10m/km
751 | d02Pump Cost | d02 | Pump Cost | €907,505.33 | Capital Investment
752 | d02Tank Cost | d02 | Tank Cost | €644,542.28 | Capital Investment
753 | d02Total Pipe Replacement Cost | d02 | Total Pipe Replacement Cost | €1,226,014.00 | Capital Investment
754 | d02Total Investment Cost | d02 | Total Investment Cost | €2,778,061.61 | Grand Total
755 | ------ | --- | --- | --- | ---
756 | Summaryfor | Summary | for | node: | d03
757 | d03Duty Head | d03 | Duty Head | 34.34 | m
758 | d03Duty Flow | d03 | Duty Flow | 102.81 | L/s
759 | d03Actual average pumped flow: | d03 | Actual average pumped flow: | 102.79 | L/s
760 | d03Cost: | d03 | Cost: | €166.02 | Europerday
761 | d03Energy: | d03 | Energy: | 1106.78 | kWh/day
762 | d03Tank Elevation | d03 | Tank Elevation | 26.86 | m above sea level
763 | d03Tank height above ground | d03 | Tank height above ground | 26.86 | m above nearest node
764 | d03Tank volume | d03 | Tank volume | 1469.6 | m3
765 | d03Minimum Pressure | d03 | Minimum Pressure | 20.1 | mwc
766 | d03Critical Hour | d03 | Critical Hour | 16 | hrs
767 | d03Critical Node | d03 | Critical Node | b12 | Node
768 | d03Critical Pipes | d03 | Critical Pipes | [] | Unit headloss >10m/km
769 | d03Pump Cost | d03 | Pump Cost | €907,505.33 | Capital Investment
770 | d03Tank Cost | d03 | Tank Cost | €638,849.57 | Capital Investment
771 | d03Total Pipe Replacement Cost | d03 | Total Pipe Replacement Cost | €1,322,224.00 | Capital Investment
772 | d03Total Investment Cost | d03 | Total Investment Cost | €2,868,578.90 | Grand Total
773 | ------ | --- | --- | --- | ---
774 | Summaryfor | Summary | for | node: | d04
775 | d04Duty Head | d04 | Duty Head | 42 | m
776 | d04Duty Flow | d04 | Duty Flow | 102.81 | L/s
777 | d04Actual average pumped flow: | d04 | Actual average pumped flow: | 102.87 | L/s
778 | d04Cost: | d04 | Cost: | €202.09 | Europerday
779 | d04Energy: | d04 | Energy: | 1347.27 | kWh/day
780 | d04Tank Elevation | d04 | Tank Elevation | 31.06 | m above sea level
781 | d04Tank height above ground | d04 | Tank height above ground | 31.06 | m above nearest node
782 | d04Tank volume | d04 | Tank volume | 1469.6 | m3
783 | d04Minimum Pressure | d04 | Minimum Pressure | 19.99 | mwc
784 | d04Critical Hour | d04 | Critical Hour | 6 | hrs
785 | d04Critical Node | d04 | Critical Node | b12 | Node
786 | d04Critical Pipes | d04 | Critical Pipes | [] | Unit headloss >10m/km
787 | d04Pump Cost | d04 | Pump Cost | €907,505.33 | Capital Investment
788 | d04Tank Cost | d04 | Tank Cost | €657,371.28 | Capital Investment
789 | d04Total Pipe Replacement Cost | d04 | Total Pipe Replacement Cost | €1,150,864.00 | Capital Investment
790 | d04Total Investment Cost | d04 | Total Investment Cost | €2,715,740.60 | Grand Total
791 | ------ | --- | --- | --- | ---
792 | Summaryfor | Summary | for | node: | d05
793 | d05Duty Head | d05 | Duty Head | 34.43 | m
794 | d05Duty Flow | d05 | Duty Flow | 102.81 | L/s
795 | d05Actual average pumped flow: | d05 | Actual average pumped flow: | 102.78 | L/s
796 | d05Cost: | d05 | Cost: | €166.43 | Europerday
797 | d05Energy: | d05 | Energy: | 1109.53 | kWh/day
798 | d05Tank Elevation | d05 | Tank Elevation | 26.94 | m above sea level
799 | d05Tank height above ground | d05 | Tank height above ground | 26.94 | m above nearest node
800 | d05Tank volume | d05 | Tank volume | 1469.6 | m3
801 | d05Minimum Pressure | d05 | Minimum Pressure | 20.1 | mwc
802 | d05Critical Hour | d05 | Critical Hour | 16 | hrs
803 | d05Critical Node | d05 | Critical Node | b12 | Node
804 | d05Critical Pipes | d05 | Critical Pipes | [] | Unit headloss >10m/km
805 | d05Pump Cost | d05 | Pump Cost | €907,505.33 | Capital Investment
806 | d05Tank Cost | d05 | Tank Cost | €639,206.90 | Capital Investment
807 | d05Total Pipe Replacement Cost | d05 | Total Pipe Replacement Cost | €1,438,864.00 | Capital Investment
808 | d05Total Investment Cost | d05 | Total Investment Cost | €2,985,576.23 | Grand Total
809 | ------ | --- | --- | --- | ---
810 | Summaryfor | Summary | for | node: | d06
811 | d06Duty Head | d06 | Duty Head | 36.41 | m
812 | d06Duty Flow | d06 | Duty Flow | 102.81 | L/s
813 | d06Actual average pumped flow: | d06 | Actual average pumped flow: | 102.84 | L/s
814 | d06Cost: | d06 | Cost: | €175.77 | Europerday
815 | d06Energy: | d06 | Energy: | 1171.81 | kWh/day
816 | d06Tank Elevation | d06 | Tank Elevation | 28.66 | m above sea level
817 | d06Tank height above ground | d06 | Tank height above ground | 28.66 | m above nearest node
818 | d06Tank volume | d06 | Tank volume | 1469.6 | m3
819 | d06Minimum Pressure | d06 | Minimum Pressure | 20.09 | mwc
820 | d06Critical Hour | d06 | Critical Hour | 6 | hrs
821 | d06Critical Node | d06 | Critical Node | b12 | Node
822 | d06Critical Pipes | d06 | Critical Pipes | [] | Unit headloss >10m/km
823 | d06Pump Cost | d06 | Pump Cost | €907,505.33 | Capital Investment
824 | d06Tank Cost | d06 | Tank Cost | €646,798.73 | Capital Investment
825 | d06Total Pipe Replacement Cost | d06 | Total Pipe Replacement Cost | €1,414,214.00 | Capital Investment
826 | d06Total Investment Cost | d06 | Total Investment Cost | €2,968,518.06 | Grand Total
827 | ------ | --- | --- | --- | ---
828 | Summaryfor | Summary | for | node: | d07
829 | d07Duty Head | d07 | Duty Head | 37.03 | m
830 | d07Duty Flow | d07 | Duty Flow | 102.81 | L/s
831 | d07Actual average pumped flow: | d07 | Actual average pumped flow: | 102.75 | L/s
832 | d07Cost: | d07 | Cost: | €178.64 | Europerday
833 | d07Energy: | d07 | Energy: | 1190.94 | kWh/day
834 | d07Tank Elevation | d07 | Tank Elevation | 29.32 | m above sea level
835 | d07Tank height above ground | d07 | Tank height above ground | 29.32 | m above nearest node
836 | d07Tank volume | d07 | Tank volume | 1469.6 | m3
837 | d07Minimum Pressure | d07 | Minimum Pressure | 20.1 | mwc
838 | d07Critical Hour | d07 | Critical Hour | 6 | hrs
839 | d07Critical Node | d07 | Critical Node | b12 | Node
840 | d07Critical Pipes | d07 | Critical Pipes | [] | Unit headloss >10m/km
841 | d07Pump Cost | d07 | Pump Cost | €907,505.33 | Capital Investment
842 | d07Tank Cost | d07 | Tank Cost | €649,715.93 | Capital Investment
843 | d07Total Pipe Replacement Cost | d07 | Total Pipe Replacement Cost | €1,490,434.00 | Capital Investment
844 | d07Total Investment Cost | d07 | Total Investment Cost | €3,047,655.26 | Grand Total
845 | ------ | --- | --- | --- | ---
846 | Summaryfor | Summary | for | node: | d08
847 | d08Duty Head | d08 | Duty Head | 37.53 | m
848 | d08Duty Flow | d08 | Duty Flow | 102.81 | L/s
849 | d08Actual average pumped flow: | d08 | Actual average pumped flow: | 102.85 | L/s
850 | d08Cost: | d08 | Cost: | €181.07 | Europerday
851 | d08Energy: | d08 | Energy: | 1207.15 | kWh/day
852 | d08Tank Elevation | d08 | Tank Elevation | 29.74 | m above sea level
853 | d08Tank height above ground | d08 | Tank height above ground | 29.74 | m above nearest node
854 | d08Tank volume | d08 | Tank volume | 1469.6 | m3
855 | d08Minimum Pressure | d08 | Minimum Pressure | 20.08 | mwc
856 | d08Critical Hour | d08 | Critical Hour | 6 | hrs
857 | d08Critical Node | d08 | Critical Node | b12 | Node
858 | d08Critical Pipes | d08 | Critical Pipes | [] | Unit headloss >10m/km
859 | d08Pump Cost | d08 | Pump Cost | €907,505.33 | Capital Investment
860 | d08Tank Cost | d08 | Tank Cost | €651,548.07 | Capital Investment
861 | d08Total Pipe Replacement Cost | d08 | Total Pipe Replacement Cost | €1,413,016.00 | Capital Investment
862 | d08Total Investment Cost | d08 | Total Investment Cost | €2,972,069.39 | Grand Total
863 | ------ | --- | --- | --- | ---
864 | Summaryfor | Summary | for | node: | e01
865 | e01Duty Head | e01 | Duty Head | 34.06 | m
866 | e01Duty Flow | e01 | Duty Flow | 102.81 | L/s
867 | e01Actual average pumped flow: | e01 | Actual average pumped flow: | 102.79 | L/s
868 | e01Cost: | e01 | Cost: | €164.68 | Europerday
869 | e01Energy: | e01 | Energy: | 1097.87 | kWh/day
870 | e01Tank Elevation | e01 | Tank Elevation | 26.57 | m above sea level
871 | e01Tank height above ground | e01 | Tank height above ground | 26.57 | m above nearest node
872 | e01Tank volume | e01 | Tank volume | 1469.6 | m3
873 | e01Minimum Pressure | e01 | Minimum Pressure | 20.1 | mwc
874 | e01Critical Hour | e01 | Critical Hour | 16 | hrs
875 | e01Critical Node | e01 | Critical Node | b12 | Node
876 | e01Critical Pipes | e01 | Critical Pipes | [] | Unit headloss >10m/km
877 | e01Pump Cost | e01 | Pump Cost | €907,505.33 | Capital Investment
878 | e01Tank Cost | e01 | Tank Cost | €637,599.17 | Capital Investment
879 | e01Total Pipe Replacement Cost | e01 | Total Pipe Replacement Cost | €1,148,364.00 | Capital Investment
880 | e01Total Investment Cost | e01 | Total Investment Cost | €2,693,468.49 | Grand Total
881 | ------ | --- | --- | --- | ---
882 | Summaryfor | Summary | for | node: | e02
883 | e02Duty Head | e02 | Duty Head | 34.19 | m
884 | e02Duty Flow | e02 | Duty Flow | 102.81 | L/s
885 | e02Actual average pumped flow: | e02 | Actual average pumped flow: | 102.76 | L/s
886 | e02Cost: | e02 | Cost: | €165.33 | Europerday
887 | e02Energy: | e02 | Energy: | 1102.19 | kWh/day
888 | e02Tank Elevation | e02 | Tank Elevation | 26.68 | m above sea level
889 | e02Tank height above ground | e02 | Tank height above ground | 26.68 | m above nearest node
890 | e02Tank volume | e02 | Tank volume | 1469.6 | m3
891 | e02Minimum Pressure | e02 | Minimum Pressure | 20.1 | mwc
892 | e02Critical Hour | e02 | Critical Hour | 16 | hrs
893 | e02Critical Node | e02 | Critical Node | b12 | Node
894 | e02Critical Pipes | e02 | Critical Pipes | [] | Unit headloss >10m/km
895 | e02Pump Cost | e02 | Pump Cost | €907,505.33 | Capital Investment
896 | e02Tank Cost | e02 | Tank Cost | €638,051.81 | Capital Investment
897 | e02Total Pipe Replacement Cost | e02 | Total Pipe Replacement Cost | €1,216,584.00 | Capital Investment
898 | e02Total Investment Cost | e02 | Total Investment Cost | €2,762,141.14 | Grand Total
899 | ------ | --- | --- | --- | ---
900 | Summaryfor | Summary | for | node: | e03
901 | e03Duty Head | e03 | Duty Head | 35.19 | m
902 | e03Duty Flow | e03 | Duty Flow | 102.81 | L/s
903 | e03Actual average pumped flow: | e03 | Actual average pumped flow: | 102.81 | L/s
904 | e03Cost: | e03 | Cost: | €169.91 | Europerday
905 | e03Energy: | e03 | Energy: | 1132.71 | kWh/day
906 | e03Tank Elevation | e03 | Tank Elevation | 27.27 | m above sea level
907 | e03Tank height above ground | e03 | Tank height above ground | 27.27 | m above nearest node
908 | e03Tank volume | e03 | Tank volume | 1469.6 | m3
909 | e03Minimum Pressure | e03 | Minimum Pressure | 19.91 | mwc
910 | e03Critical Hour | e03 | Critical Hour | 16 | hrs
911 | e03Critical Node | e03 | Critical Node | b12 | Node
912 | e03Critical Pipes | e03 | Critical Pipes | [] | Unit headloss >10m/km
913 | e03Pump Cost | e03 | Pump Cost | €907,505.33 | Capital Investment
914 | e03Tank Cost | e03 | Tank Cost | €640,681.32 | Capital Investment
915 | e03Total Pipe Replacement Cost | e03 | Total Pipe Replacement Cost | €1,287,324.00 | Capital Investment
916 | e03Total Investment Cost | e03 | Total Investment Cost | €2,835,510.64 | Grand Total
917 | ------ | --- | --- | --- | ---
918 | Summaryfor | Summary | for | node: | e04
919 | e04Duty Head | e04 | Duty Head | 36.05 | m
920 | e04Duty Flow | e04 | Duty Flow | 102.81 | L/s
921 | e04Actual average pumped flow: | e04 | Actual average pumped flow: | 102.72 | L/s
922 | e04Cost: | e04 | Cost: | €173.93 | Europerday
923 | e04Energy: | e04 | Energy: | 1159.54 | kWh/day
924 | e04Tank Elevation | e04 | Tank Elevation | 28.12 | m above sea level
925 | e04Tank height above ground | e04 | Tank height above ground | 28.12 | m above nearest node
926 | e04Tank volume | e04 | Tank volume | 1469.6 | m3
927 | e04Minimum Pressure | e04 | Minimum Pressure | 20.1 | mwc
928 | e04Critical Hour | e04 | Critical Hour | 6 | hrs
929 | e04Critical Node | e04 | Critical Node | b12 | Node
930 | e04Critical Pipes | e04 | Critical Pipes | [] | Unit headloss >10m/km
931 | e04Pump Cost | e04 | Pump Cost | €907,505.33 | Capital Investment
932 | e04Tank Cost | e04 | Tank Cost | €644,428.06 | Capital Investment
933 | e04Total Pipe Replacement Cost | e04 | Total Pipe Replacement Cost | €1,417,614.00 | Capital Investment
934 | e04Total Investment Cost | e04 | Total Investment Cost | €2,969,547.39 | Grand Total
935 | ------ | --- | --- | --- | ---
936 | Summaryfor | Summary | for | node: | e05
937 | e05Duty Head | e05 | Duty Head | 37.38 | m
938 | e05Duty Flow | e05 | Duty Flow | 102.81 | L/s
939 | e05Actual average pumped flow: | e05 | Actual average pumped flow: | 102.85 | L/s
940 | e05Cost: | e05 | Cost: | €180.27 | Europerday
941 | e05Energy: | e05 | Energy: | 1201.83 | kWh/day
942 | e05Tank Elevation | e05 | Tank Elevation | 29.31 | m above sea level
943 | e05Tank height above ground | e05 | Tank height above ground | 29.31 | m above nearest node
944 | e05Tank volume | e05 | Tank volume | 1469.6 | m3
945 | e05Minimum Pressure | e05 | Minimum Pressure | 20.08 | mwc
946 | e05Critical Hour | e05 | Critical Hour | 6 | hrs
947 | e05Critical Node | e05 | Critical Node | b12 | Node
948 | e05Critical Pipes | e05 | Critical Pipes | [] | Unit headloss >10m/km
949 | e05Pump Cost | e05 | Pump Cost | €907,505.33 | Capital Investment
950 | e05Tank Cost | e05 | Tank Cost | €649,678.42 | Capital Investment
951 | e05Total Pipe Replacement Cost | e05 | Total Pipe Replacement Cost | €1,449,198.00 | Capital Investment
952 | e05Total Investment Cost | e05 | Total Investment Cost | €3,006,381.75 | Grand Total
953 | ------ | --- | --- | --- | ---
954 | Summaryfor | Summary | for | node: | e06
955 | e06Duty Head | e06 | Duty Head | 35.02 | m
956 | e06Duty Flow | e06 | Duty Flow | 102.81 | L/s
957 | e06Actual average pumped flow: | e06 | Actual average pumped flow: | 102.78 | L/s
958 | e06Cost: | e06 | Cost: | €169.16 | Europerday
959 | e06Energy: | e06 | Energy: | 1127.75 | kWh/day
960 | e06Tank Elevation | e06 | Tank Elevation | 27.4 | m above sea level
961 | e06Tank height above ground | e06 | Tank height above ground | 27.4 | m above nearest node
962 | e06Tank volume | e06 | Tank volume | 1469.6 | m3
963 | e06Minimum Pressure | e06 | Minimum Pressure | 20.1 | mwc
964 | e06Critical Hour | e06 | Critical Hour | 16 | hrs
965 | e06Critical Node | e06 | Critical Node | b12 | Node
966 | e06Critical Pipes | e06 | Critical Pipes | [] | Unit headloss >10m/km
967 | e06Pump Cost | e06 | Pump Cost | €907,505.33 | Capital Investment
968 | e06Tank Cost | e06 | Tank Cost | €641,230.30 | Capital Investment
969 | e06Total Pipe Replacement Cost | e06 | Total Pipe Replacement Cost | €1,466,163.00 | Capital Investment
970 | e06Total Investment Cost | e06 | Total Investment Cost | €3,014,898.63 | Grand Total
971 | ------ | --- | --- | --- | ---
972 | Summaryfor | Summary | for | node: | e07
973 | e07Duty Head | e07 | Duty Head | 35.8 | m
974 | e07Duty Flow | e07 | Duty Flow | 102.81 | L/s
975 | e07Actual average pumped flow: | e07 | Actual average pumped flow: | 102.81 | L/s
976 | e07Cost: | e07 | Cost: | €172.79 | Europerday
977 | e07Energy: | e07 | Energy: | 1151.93 | kWh/day
978 | e07Tank Elevation | e07 | Tank Elevation | 27.82 | m above sea level
979 | e07Tank height above ground | e07 | Tank height above ground | 27.82 | m above nearest node
980 | e07Tank volume | e07 | Tank volume | 1469.6 | m3
981 | e07Minimum Pressure | e07 | Minimum Pressure | 19.97 | mwc
982 | e07Critical Hour | e07 | Critical Hour | 6 | hrs
983 | e07Critical Node | e07 | Critical Node | b12 | Node
984 | e07Critical Pipes | e07 | Critical Pipes | [] | Unit headloss >10m/km
985 | e07Pump Cost | e07 | Pump Cost | €907,505.33 | Capital Investment
986 | e07Tank Cost | e07 | Tank Cost | €643,102.56 | Capital Investment
987 | e07Total Pipe Replacement Cost | e07 | Total Pipe Replacement Cost | €1,496,404.00 | Capital Investment
988 | e07Total Investment Cost | e07 | Total Investment Cost | €3,047,011.89 | Grand Total
989 | ------ | --- | --- | --- | ---
990 | Summaryfor | Summary | for | node: | e08
991 | e08Duty Head | e08 | Duty Head | 36.47 | m
992 | e08Duty Flow | e08 | Duty Flow | 102.81 | L/s
993 | e08Actual average pumped flow: | e08 | Actual average pumped flow: | 102.74 | L/s
994 | e08Cost: | e08 | Cost: | €175.91 | Europerday
995 | e08Energy: | e08 | Energy: | 1172.75 | kWh/day
996 | e08Tank Elevation | e08 | Tank Elevation | 28.48 | m above sea level
997 | e08Tank height above ground | e08 | Tank height above ground | 28.48 | m above nearest node
998 | e08Tank volume | e08 | Tank volume | 1469.6 | m3
999 | e08Minimum Pressure | e08 | Minimum Pressure | 20.1 | mwc
1000 | e08Critical Hour | e08 | Critical Hour | 6 | hrs
1001 | e08Critical Node | e08 | Critical Node | b12 | Node
1002 | e08Critical Pipes | e08 | Critical Pipes | [] | Unit headloss >10m/km
1003 | e08Pump Cost | e08 | Pump Cost | €907,505.33 | Capital Investment
1004 | e08Tank Cost | e08 | Tank Cost | €646,017.16 | Capital Investment
1005 | e08Total Pipe Replacement Cost | e08 | Total Pipe Replacement Cost | €1,593,189.00 | Capital Investment
1006 | e08Total Investment Cost | e08 | Total Investment Cost | €3,146,711.49 | Grand Total
1007 | ------ | --- | --- | --- | ---
1008 | Summaryfor | Summary | for | node: | f01
1009 | f01Duty Head | f01 | Duty Head | 34.44 | m
1010 | f01Duty Flow | f01 | Duty Flow | 102.81 | L/s
1011 | f01Actual average pumped flow: | f01 | Actual average pumped flow: | 102.78 | L/s
1012 | f01Cost: | f01 | Cost: | €166.44 | Europerday
1013 | f01Energy: | f01 | Energy: | 1109.63 | kWh/day
1014 | f01Tank Elevation | f01 | Tank Elevation | 26.82 | m above sea level
1015 | f01Tank height above ground | f01 | Tank height above ground | 26.82 | m above nearest node
1016 | f01Tank volume | f01 | Tank volume | 1469.6 | m3
1017 | f01Minimum Pressure | f01 | Minimum Pressure | 20.1 | mwc
1018 | f01Critical Hour | f01 | Critical Hour | 16 | hrs
1019 | f01Critical Node | f01 | Critical Node | b12 | Node
1020 | f01Critical Pipes | f01 | Critical Pipes | [] | Unit headloss >10m/km
1021 | f01Pump Cost | f01 | Pump Cost | €907,505.33 | Capital Investment
1022 | f01Tank Cost | f01 | Tank Cost | €638,698.18 | Capital Investment
1023 | f01Total Pipe Replacement Cost | f01 | Total Pipe Replacement Cost | €1,423,724.00 | Capital Investment
1024 | f01Total Investment Cost | f01 | Total Investment Cost | €2,969,927.51 | Grand Total
1025 | ------ | --- | --- | --- | ---

## a01
This sheet contains the results for tank connected to node: a01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.57 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | e05
Cost: | €225.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1502.89 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 42.62 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 42.62 | m above nearest node |  | Tank Cost | €708,340.50
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,141,879.83
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a02
This sheet contains the results for tank connected to node: a02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.58 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €215.78 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1438.55 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 39.57 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 39.57 | m above nearest node |  | Tank Cost | €694,890.21
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,128,429.53
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
| 0.08 | 380 | 0.1 | 90 | 34200
| 0.08 | 249 | 0.1 | 90 | 22410
| 0.1 | 256 | 0.125 | 110 | 28160
| 0.08 | 111 | 0.1 | 90 | 9990
| 0.1 | 459 | 0.125 | 110 | 50490
| 0.1 | 168 | 0.125 | 110 | 18480
| 0.08 | 291 | 0.1 | 90 | 26190
| 0.08 | 106 | 0.1 | 90 | 9540
| 0.05 | 290 | 0.08 | 72 | 20880
| 0.05 | 269 | 0.08 | 72 | 19368
| 0.05 | 333 | 0.08 | 72 | 23976
| 0.08 | 380 | 0.1 | 90 | 34200
| 0.08 | 177 | 0.1 | 90 | 15930
| 0.15 | 361 | 0.2 | 180 | 64980
| 0.15 | 366 | 0.2 | 180 | 65880
| 0.15 | 452 | 0.2 | 180 | 81360

## a03
This sheet contains the results for tank connected to node: a03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.17 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €213.81 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1425.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 39.02 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 39.02 | m above nearest node |  | Tank Cost | €692,488.29
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €701,174.00
|  |  |  | Total Investment Cost | €2,301,167.61
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.3 | 270 | 102600
p05 | 0.08 | 325 | 0.25 | 225 | 73125
p07 | 0.08 | 249 | 0.25 | 225 | 56025
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a04
This sheet contains the results for tank connected to node: a04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.58 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €210.96 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1406.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.04 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 38.04 | m above nearest node |  | Tank Cost | €688,136.32
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,121,675.65
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a05
This sheet contains the results for tank connected to node: a05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.62 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | €211.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1407.77 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.21 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 38.21 | m above nearest node |  | Tank Cost | €688,891.78
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €695,279.00
|  |  |  | Total Investment Cost | €2,291,676.11
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.25 | 225 | 85500
p05 | 0.08 | 325 | 0.25 | 225 | 73125
p07 | 0.08 | 249 | 0.3 | 270 | 67230
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a06
This sheet contains the results for tank connected to node: a06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.12 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €208.71 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1391.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.33 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 37.33 | m above nearest node |  | Tank Cost | €685,018.03
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,118,557.36
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a07
This sheet contains the results for tank connected to node: a07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.82 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €207.26 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1381.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.87 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.87 | m above nearest node |  | Tank Cost | €682,991.43
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,116,530.76
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a08
This sheet contains the results for tank connected to node: a08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.74 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | €206.89 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1379.28 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.77 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.77 | m above nearest node |  | Tank Cost | €682,568.77
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €790,869.00
|  |  |  | Total Investment Cost | €2,380,943.10
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.2 | 180 | 36000
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p12 | 0.08 | 106 | 0.1 | 90 | 9540
p13 | 0.08 | 215 | 0.1 | 90 | 19350
p16 | 0.025 | 168 | 0.05 | 45 | 7560
p18 | 0.1 | 420 | 0.2 | 180 | 75600
p19 | 0.1 | 459 | 0.25 | 225 | 103275
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a09
This sheet contains the results for tank connected to node: a09
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | €208.03 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1386.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.87 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.87 | m above nearest node |  | Tank Cost | €682,981.52
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €833,700.00
|  |  |  | Total Investment Cost | €2,424,186.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.3 | 270 | 69120
p10 | 0.1 | 200 | 0.3 | 270 | 54000
p11 | 0.08 | 111 | 0.2 | 180 | 19980
p12 | 0.08 | 106 | 0.15 | 135 | 14310
p13 | 0.08 | 215 | 0.15 | 135 | 29025
p16 | 0.025 | 168 | 0.08 | 72 | 12096
p18 | 0.1 | 420 | 0.25 | 225 | 94500
p19 | 0.1 | 459 | 0.25 | 225 | 103275
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a10
This sheet contains the results for tank connected to node: a10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.8 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.8 | L/s |  | Critical Node | e05
Cost: | €207.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1380.41 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.76 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.76 | m above nearest node |  | Tank Cost | €682,504.44
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €890,584.00
|  |  |  | Total Investment Cost | €2,480,593.77
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.125 | 110 | 22000
p11 | 0.08 | 111 | 0.4 | 360 | 39960
p12 | 0.08 | 106 | 0.2 | 180 | 19080
p13 | 0.08 | 215 | 0.2 | 180 | 38700
p14 | 0.08 | 369 | 0.1 | 90 | 33210
p15 | 0.08 | 386 | 0.1 | 90 | 34740
p16 | 0.025 | 168 | 0.1 | 90 | 15120
p18 | 0.1 | 420 | 0.2 | 180 | 75600
p19 | 0.1 | 459 | 0.2 | 180 | 82620
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a11
This sheet contains the results for tank connected to node: a11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.6 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | e05
Cost: | €210.96 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1406.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.5 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 37.5 | m above nearest node |  | Tank Cost | €685,759.83
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €901,659.00
|  |  |  | Total Investment Cost | €2,494,924.16
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.3 | 270 | 69120
p10 | 0.1 | 200 | 0.2 | 180 | 36000
p11 | 0.08 | 111 | 0.25 | 225 | 24975
p12 | 0.08 | 106 | 0.25 | 225 | 23850
p13 | 0.08 | 215 | 0.25 | 225 | 48375
p14 | 0.08 | 369 | 0.1 | 90 | 33210
p15 | 0.08 | 386 | 0.1 | 90 | 34740
p16 | 0.025 | 168 | 0.1 | 90 | 15120
p18 | 0.1 | 420 | 0.2 | 180 | 75600
p19 | 0.1 | 459 | 0.25 | 225 | 103275
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a12
This sheet contains the results for tank connected to node: a12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.96 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €212.71 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1418.09 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.94 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 37.94 | m above nearest node |  | Tank Cost | €687,727.54
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €942,969.00
|  |  |  | Total Investment Cost | €2,538,201.87
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.15 | 135 | 27000
p11 | 0.08 | 111 | 0.3 | 270 | 29970
p12 | 0.08 | 106 | 0.2 | 180 | 19080
p13 | 0.08 | 215 | 0.1 | 90 | 19350
p14 | 0.08 | 369 | 0.3 | 270 | 99630
p15 | 0.08 | 386 | 0.2 | 180 | 69480
p16 | 0.025 | 168 | 0.2 | 180 | 30240
p18 | 0.1 | 420 | 0.15 | 135 | 56700
p19 | 0.1 | 459 | 0.15 | 135 | 61965
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a13
This sheet contains the results for tank connected to node: a13
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.2 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €213.77 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1425.13 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.12 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 38.12 | m above nearest node |  | Tank Cost | €688,490.89
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,002,279.00
|  |  |  | Total Investment Cost | €2,598,275.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.25 | 225 | 45000
p11 | 0.08 | 111 | 0.25 | 225 | 24975
p12 | 0.08 | 106 | 0.25 | 225 | 23850
p13 | 0.08 | 215 | 0.2 | 180 | 38700
p14 | 0.08 | 369 | 0.2 | 180 | 66420
p15 | 0.08 | 386 | 0.3 | 270 | 104220
p16 | 0.025 | 168 | 0.2 | 180 | 30240
p18 | 0.1 | 420 | 0.15 | 135 | 56700
p19 | 0.1 | 459 | 0.2 | 180 | 82620
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a14
This sheet contains the results for tank connected to node: a14
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.99 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €203.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1355.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35.6 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 35.6 | m above nearest node |  | Tank Cost | €677,414.25
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,110,953.58
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a15
This sheet contains the results for tank connected to node: a15
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.78 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | e05
Cost: | €207.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1380.4 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.55 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.55 | m above nearest node |  | Tank Cost | €681,594.94
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €813,504.00
|  |  |  | Total Investment Cost | €2,402,604.27
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.25 | 225 | 57600
p10 | 0.1 | 200 | 0.25 | 225 | 45000
p11 | 0.08 | 111 | 0.125 | 110 | 12210
p12 | 0.08 | 106 | 0.125 | 110 | 11660
p13 | 0.08 | 215 | 0.125 | 110 | 23650
p16 | 0.025 | 168 | 0.05 | 45 | 7560
p18 | 0.1 | 420 | 0.25 | 225 | 94500
p19 | 0.1 | 459 | 0.3 | 270 | 123930
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a16
This sheet contains the results for tank connected to node: a16
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.79 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €202.26 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1348.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35.27 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 35.27 | m above nearest node |  | Tank Cost | €675,938.21
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,109,477.54
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a17
This sheet contains the results for tank connected to node: a17
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.09 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | €198.90 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1325.99 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 34.5 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 34.5 | m above nearest node |  | Tank Cost | €672,548.31
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €695,444.00
|  |  |  | Total Investment Cost | €2,275,497.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.3 | 270 | 45360
p22 | 0.08 | 291 | 0.125 | 110 | 32010
p24 | 0.08 | 255 | 0.2 | 180 | 45900
p25 | 0.05 | 206 | 0.125 | 110 | 22660
p26 | 0.1 | 202 | 0.2 | 180 | 36360
p27 | 0.08 | 289 | 0.125 | 110 | 31790
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a18
This sheet contains the results for tank connected to node: a18
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.73 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €201.85 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1345.67 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 35 | m above nearest node |  | Tank Cost | €674,742.30
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €730,754.00
|  |  |  | Total Investment Cost | €2,313,001.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.3 | 270 | 45360
p22 | 0.08 | 291 | 0.3 | 270 | 78570
p25 | 0.05 | 206 | 0.2 | 180 | 37080
p26 | 0.1 | 202 | 0.2 | 180 | 36360
p27 | 0.08 | 289 | 0.2 | 180 | 52020
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a19
This sheet contains the results for tank connected to node: a19
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.54 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €191.32 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1275.49 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 32.75 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 32.75 | m above nearest node |  | Tank Cost | €664,811.36
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €628,994.00
|  |  |  | Total Investment Cost | €2,201,310.69
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a20
This sheet contains the results for tank connected to node: a20
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.76 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | €192.40 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1282.69 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 33.08 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 33.08 | m above nearest node |  | Tank Cost | €666,282.10
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €823,739.00
|  |  |  | Total Investment Cost | €2,397,526.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.25 | 225 | 37800
p22 | 0.08 | 291 | 0.125 | 110 | 32010
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.25 | 225 | 57375
p25 | 0.05 | 206 | 0.125 | 110 | 22660
p26 | 0.1 | 202 | 0.3 | 270 | 54540
p27 | 0.08 | 289 | 0.125 | 110 | 31790
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a21
This sheet contains the results for tank connected to node: a21
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.09 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €194.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1293.46 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 33.43 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 33.43 | m above nearest node |  | Tank Cost | €667,817.26
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €892,709.00
|  |  |  | Total Investment Cost | €2,468,031.59
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.25 | 225 | 37800
p22 | 0.08 | 291 | 0.25 | 225 | 65475
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p25 | 0.05 | 206 | 0.25 | 225 | 46350
p26 | 0.1 | 202 | 0.3 | 270 | 54540
p27 | 0.08 | 289 | 0.3 | 270 | 78030
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b01
This sheet contains the results for tank connected to node: b01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.16 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | €179.83 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1198.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.1 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.1 | m above nearest node |  | Tank Cost | €653,165.04
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €762,914.00
|  |  |  | Total Investment Cost | €2,323,584.37
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b02
This sheet contains the results for tank connected to node: b02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.29 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.72 | L/s |  | Critical Node | e05
Cost: | €180.42 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1202.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.17 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.17 | m above nearest node |  | Tank Cost | €653,460.44
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €901,514.00
|  |  |  | Total Investment Cost | €2,462,479.77
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b03
This sheet contains the results for tank connected to node: b03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.41 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €180.97 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1206.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.17 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.17 | m above nearest node |  | Tank Cost | €653,475.24
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €990,794.00
|  |  |  | Total Investment Cost | €2,551,774.57
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b04
This sheet contains the results for tank connected to node: b04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.55 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | €181.61 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1210.74 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.31 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.31 | m above nearest node |  | Tank Cost | €654,079.77
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,123,368.00
|  |  |  | Total Investment Cost | €2,684,953.10
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.4 | 360 | 100080
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.1 | 90 | 26100
p36 | 0.05 | 269 | 0.1 | 90 | 24210
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b05
This sheet contains the results for tank connected to node: b05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.37 | m |  | Minimum Pressure | 19.95 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €185.41 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1236.1 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.92 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.92 | m above nearest node |  | Tank Cost | €656,758.23
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,230,660.00
|  |  |  | Total Investment Cost | €2,794,923.56
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.3 | 270 | 75060
p32 | 0.125 | 270 | 0.3 | 270 | 72900
p33 | 0.08 | 106 | 0.125 | 110 | 11660
p34 | 0.05 | 290 | 0.125 | 110 | 31900
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.125 | 110 | 29590
p37 | 0.05 | 333 | 0.125 | 110 | 36630
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b06
This sheet contains the results for tank connected to node: b06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.62 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €181.93 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1212.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.36 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.36 | m above nearest node |  | Tank Cost | €654,282.57
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,175,820.00
|  |  |  | Total Investment Cost | €2,737,607.89
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.125 | 110 | 11660
p34 | 0.05 | 290 | 0.125 | 110 | 31900
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.125 | 110 | 36630
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p39 | 0.125 | 380 | 0.4 | 360 | 136800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b07
This sheet contains the results for tank connected to node: b07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.34 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €185.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1235.26 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.94 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.94 | m above nearest node |  | Tank Cost | €656,852.15
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,195,773.00
|  |  |  | Total Investment Cost | €2,760,130.47
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p32 | 0.125 | 270 | 0.15 | 135 | 36450
p33 | 0.08 | 106 | 0.3 | 270 | 28620
p34 | 0.05 | 290 | 0.15 | 135 | 39150
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.15 | 135 | 44955
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p39 | 0.125 | 380 | 0.3 | 270 | 102600
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b08
This sheet contains the results for tank connected to node: b08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.67 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €186.82 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1245.47 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.25 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31.25 | m above nearest node |  | Tank Cost | €658,217.49
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,321,665.00
|  |  |  | Total Investment Cost | €2,887,387.82
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.25 | 225 | 62550
p32 | 0.125 | 270 | 0.25 | 225 | 60750
p33 | 0.08 | 106 | 0.25 | 225 | 23850
p34 | 0.05 | 290 | 0.25 | 225 | 65250
p36 | 0.05 | 269 | 0.1 | 90 | 24210
p37 | 0.05 | 333 | 0.25 | 225 | 74925
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p39 | 0.125 | 380 | 0.25 | 225 | 85500
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b09
This sheet contains the results for tank connected to node: b09
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.59 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €181.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1211.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.34 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.34 | m above nearest node |  | Tank Cost | €654,219.18
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,175,778.00
|  |  |  | Total Investment Cost | €2,737,502.51
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.125 | 110 | 29590
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p40 | 0.125 | 289 | 0.4 | 360 | 104040
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b10
This sheet contains the results for tank connected to node: b10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.34 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €185.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1235.28 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31 | m above nearest node |  | Tank Cost | €657,119.84
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,180,008.00
|  |  |  | Total Investment Cost | €2,744,633.17
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.125 | 110 | 29590
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p40 | 0.125 | 289 | 0.3 | 270 | 78030
p41 | 0.125 | 112 | 0.3 | 270 | 30240
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b11
This sheet contains the results for tank connected to node: b11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.13 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | e05
Cost: | €193.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1290.91 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 32.17 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 32.17 | m above nearest node |  | Tank Cost | €662,259.66
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,231,931.00
|  |  |  | Total Investment Cost | €2,801,695.99
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.3 | 270 | 101520
p30 | 0.2 | 248 | 0.3 | 270 | 66960
p32 | 0.125 | 270 | 0.15 | 135 | 36450
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.3 | 270 | 118530
p36 | 0.05 | 269 | 0.15 | 135 | 36315
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.15 | 135 | 51300
p40 | 0.125 | 289 | 0.3 | 270 | 78030
p41 | 0.125 | 112 | 0.3 | 270 | 30240
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b12
This sheet contains the results for tank connected to node: b12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.68 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €186.88 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1245.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.21 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31.21 | m above nearest node |  | Tank Cost | €658,026.79
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,415,572.00
|  |  |  | Total Investment Cost | €2,981,104.11
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.3 | 270 | 75060
p32 | 0.125 | 270 | 0.3 | 270 | 72900
p33 | 0.08 | 106 | 0.125 | 110 | 11660
p34 | 0.05 | 290 | 0.1 | 90 | 26100
p35 | 0.1 | 439 | 0.2 | 180 | 79020
p36 | 0.05 | 269 | 0.2 | 180 | 48420
p37 | 0.05 | 333 | 0.1 | 90 | 29970
p38 | 0.08 | 380 | 0.3 | 270 | 102600
p40 | 0.125 | 289 | 0.2 | 180 | 52020
p41 | 0.125 | 112 | 0.2 | 180 | 20160
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c01
This sheet contains the results for tank connected to node: c01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €164.41 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1096.04 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.57 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.57 | m above nearest node |  | Tank Cost | €637,571.18
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,049,974.00
|  |  |  | Total Investment Cost | €2,595,050.51
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c02
This sheet contains the results for tank connected to node: c02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.09 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | b12
Cost: | €164.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1098.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.65 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.65 | m above nearest node |  | Tank Cost | €637,940.03
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,198,284.00
|  |  |  | Total Investment Cost | €2,743,729.36
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.125 | 110 | 17490
p56 | 0.1 | 349 | 0.125 | 110 | 38390
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c03
This sheet contains the results for tank connected to node: c03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.74 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €167.85 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1119.03 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.16 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.16 | m above nearest node |  | Tank Cost | €640,173.89
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,269,619.00
|  |  |  | Total Investment Cost | €2,817,298.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p53 | 0.1 | 177 | 0.3 | 270 | 47790
p54 | 0.08 | 177 | 0.15 | 135 | 23895
p55 | 0.08 | 159 | 0.15 | 135 | 21465
p56 | 0.1 | 349 | 0.15 | 135 | 47115
p57 | 0.125 | 108 | 0.2 | 180 | 19440
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c04
This sheet contains the results for tank connected to node: c04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.91 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €168.69 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1124.6 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.33 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.33 | m above nearest node |  | Tank Cost | €640,915.06
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,332,844.00
|  |  |  | Total Investment Cost | €2,881,264.38
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p53 | 0.1 | 177 | 0.3 | 270 | 47790
p54 | 0.08 | 177 | 0.3 | 270 | 47790
p55 | 0.08 | 159 | 0.2 | 180 | 28620
p56 | 0.1 | 349 | 0.2 | 180 | 62820
p57 | 0.125 | 108 | 0.2 | 180 | 19440
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.25 | 225 | 82350
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c05
This sheet contains the results for tank connected to node: c05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.22 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €165.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1102.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.67 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.67 | m above nearest node |  | Tank Cost | €638,022.14
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,296,246.00
|  |  |  | Total Investment Cost | €2,841,773.47
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p53 | 0.1 | 177 | 0.125 | 110 | 19470
p54 | 0.08 | 177 | 0.125 | 110 | 19470
p55 | 0.08 | 159 | 0.125 | 110 | 17490
p56 | 0.1 | 349 | 0.125 | 110 | 38390
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.4 | 360 | 131760
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c06
This sheet contains the results for tank connected to node: c06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €169.03 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1126.89 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.11 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.11 | m above nearest node |  | Tank Cost | €639,955.10
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,317,184.00
|  |  |  | Total Investment Cost | €2,864,644.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.2 | 180 | 33120
p53 | 0.1 | 177 | 0.15 | 135 | 23895
p54 | 0.08 | 177 | 0.15 | 135 | 23895
p55 | 0.08 | 159 | 0.15 | 135 | 21465
p56 | 0.1 | 349 | 0.15 | 135 | 47115
p57 | 0.125 | 108 | 0.3 | 270 | 29160
p58 | 0.25 | 168 | 0.3 | 270 | 45360
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.3 | 270 | 98820
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c07
This sheet contains the results for tank connected to node: c07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.38 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | b12
Cost: | €170.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1138.92 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.56 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.56 | m above nearest node |  | Tank Cost | €641,962.19
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,336,354.00
|  |  |  | Total Investment Cost | €2,885,821.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.25 | 225 | 41400
p53 | 0.1 | 177 | 0.25 | 225 | 39825
p54 | 0.08 | 177 | 0.25 | 225 | 39825
p55 | 0.08 | 159 | 0.25 | 225 | 35775
p56 | 0.1 | 349 | 0.25 | 225 | 78525
p57 | 0.125 | 108 | 0.25 | 225 | 24300
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.25 | 225 | 82350
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d01
This sheet contains the results for tank connected to node: d01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.22 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €165.46 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1103.05 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.75 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.75 | m above nearest node |  | Tank Cost | €638,392.26
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,229,074.00
|  |  |  | Total Investment Cost | €2,774,971.58
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p44 | 0.15 | 201 | 0.4 | 360 | 72360
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d02
This sheet contains the results for tank connected to node: d02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.79 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | b12
Cost: | €172.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1152.27 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.15 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.15 | m above nearest node |  | Tank Cost | €644,542.28
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,226,014.00
|  |  |  | Total Investment Cost | €2,778,061.61
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p45 | 0.05 | 214 | 0.3 | 270 | 57780
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d03
This sheet contains the results for tank connected to node: d03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.34 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | b12
Cost: | €166.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1106.78 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.86 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.86 | m above nearest node |  | Tank Cost | €638,849.57
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,322,224.00
|  |  |  | Total Investment Cost | €2,868,578.90
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p44 | 0.15 | 201 | 0.4 | 360 | 72360
p46 | 0.15 | 195 | 0.4 | 360 | 70200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d04
This sheet contains the results for tank connected to node: d04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.87 | L/s |  | Critical Node | b12
Cost: | €202.09 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1347.27 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.06 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31.06 | m above nearest node |  | Tank Cost | €657,371.28
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,150,864.00
|  |  |  | Total Investment Cost | €2,715,740.60
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.3 | 270 | 196290
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.2 | 180 | 24480
p48 | 0.08 | 461 | 0.25 | 225 | 103725
p49 | 0.05 | 148 | 0.15 | 135 | 19980
p50 | 0.1 | 85 | 0.15 | 135 | 11475
p51 | 0.05 | 368 | 0.15 | 135 | 49680
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d05
This sheet contains the results for tank connected to node: d05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €166.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1109.53 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.94 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.94 | m above nearest node |  | Tank Cost | €639,206.90
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,438,864.00
|  |  |  | Total Investment Cost | €2,985,576.23
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p44 | 0.15 | 201 | 0.4 | 360 | 72360
p46 | 0.15 | 195 | 0.4 | 360 | 70200
p47 | 0.1 | 136 | 0.4 | 360 | 48960
p48 | 0.08 | 461 | 0.125 | 110 | 50710
p49 | 0.05 | 148 | 0.125 | 110 | 16280
p50 | 0.1 | 85 | 0.125 | 110 | 9350
p51 | 0.05 | 368 | 0.125 | 110 | 40480
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d06
This sheet contains the results for tank connected to node: d06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.41 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | b12
Cost: | €175.77 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1171.81 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.66 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.66 | m above nearest node |  | Tank Cost | €646,798.73
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,414,214.00
|  |  |  | Total Investment Cost | €2,968,518.06
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.3 | 270 | 36720
p48 | 0.08 | 461 | 0.125 | 110 | 50710
p49 | 0.05 | 148 | 0.125 | 110 | 16280
p50 | 0.1 | 85 | 0.3 | 270 | 22950
p51 | 0.05 | 368 | 0.125 | 110 | 40480
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d07
This sheet contains the results for tank connected to node: d07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.03 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | b12
Cost: | €178.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1190.94 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 29.32 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 29.32 | m above nearest node |  | Tank Cost | €649,715.93
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,490,434.00
|  |  |  | Total Investment Cost | €3,047,655.26
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.25 | 225 | 30600
p48 | 0.08 | 461 | 0.25 | 225 | 103725
p49 | 0.05 | 148 | 0.25 | 225 | 33300
p50 | 0.1 | 85 | 0.25 | 225 | 19125
p51 | 0.05 | 368 | 0.25 | 225 | 82800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d08
This sheet contains the results for tank connected to node: d08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.53 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.85 | L/s |  | Critical Node | b12
Cost: | €181.07 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1207.15 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 29.74 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 29.74 | m above nearest node |  | Tank Cost | €651,548.07
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,413,016.00
|  |  |  | Total Investment Cost | €2,972,069.39
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.3 | 270 | 36720
p49 | 0.05 | 148 | 0.08 | 72 | 10656
p50 | 0.1 | 85 | 0.3 | 270 | 22950
p51 | 0.05 | 368 | 0.08 | 72 | 26496
p52 | 0.08 | 256 | 0.3 | 270 | 69120
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e01
This sheet contains the results for tank connected to node: e01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.06 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | b12
Cost: | €164.68 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1097.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.57 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.57 | m above nearest node |  | Tank Cost | €637,599.17
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,148,364.00
|  |  |  | Total Investment Cost | €2,693,468.49
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e02
This sheet contains the results for tank connected to node: e02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.19 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | b12
Cost: | €165.33 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1102.19 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.68 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.68 | m above nearest node |  | Tank Cost | €638,051.81
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,216,584.00
|  |  |  | Total Investment Cost | €2,762,141.14
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.4 | 360 | 129960
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e03
This sheet contains the results for tank connected to node: e03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.19 | m |  | Minimum Pressure | 19.91 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €169.91 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1132.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.27 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.27 | m above nearest node |  | Tank Cost | €640,681.32
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,287,324.00
|  |  |  | Total Investment Cost | €2,835,510.64
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p66 | 0.05 | 280 | 0.1 | 90 | 25200
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e04
This sheet contains the results for tank connected to node: e04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.05 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.72 | L/s |  | Critical Node | b12
Cost: | €173.93 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1159.54 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.12 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.12 | m above nearest node |  | Tank Cost | €644,428.06
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,417,614.00
|  |  |  | Total Investment Cost | €2,969,547.39
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p61 | 0.125 | 277 | 0.3 | 270 | 74790
p65 | 0.08 | 272 | 0.1 | 90 | 24480
p66 | 0.05 | 280 | 0.1 | 90 | 25200
p67 | 0.05 | 282 | 0.125 | 110 | 31020
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e05
This sheet contains the results for tank connected to node: e05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.38 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.85 | L/s |  | Critical Node | b12
Cost: | €180.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1201.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 29.31 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 29.31 | m above nearest node |  | Tank Cost | €649,678.42
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,449,198.00
|  |  |  | Total Investment Cost | €3,006,381.75
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p61 | 0.125 | 277 | 0.3 | 270 | 74790
p62 | 0.08 | 266 | 0.3 | 270 | 71820
p66 | 0.05 | 280 | 0.08 | 72 | 20160
p67 | 0.05 | 282 | 0.08 | 72 | 20304
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e06
This sheet contains the results for tank connected to node: e06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.02 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €169.16 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1127.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.4 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.4 | m above nearest node |  | Tank Cost | €641,230.30
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,466,163.00
|  |  |  | Total Investment Cost | €3,014,898.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.4 | 360 | 129960
p60 | 0.15 | 289 | 0.2 | 180 | 52020
p63 | 0.1 | 354 | 0.3 | 270 | 95580
p64 | 0.1 | 325 | 0.15 | 135 | 43875
p66 | 0.05 | 280 | 0.15 | 135 | 37800
p67 | 0.05 | 282 | 0.08 | 72 | 20304
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e07
This sheet contains the results for tank connected to node: e07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.8 | m |  | Minimum Pressure | 19.97 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €172.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1151.93 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.82 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.82 | m above nearest node |  | Tank Cost | €643,102.56
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,496,404.00
|  |  |  | Total Investment Cost | €3,047,011.89
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p63 | 0.1 | 354 | 0.15 | 135 | 47790
p64 | 0.1 | 325 | 0.3 | 270 | 87750
p65 | 0.08 | 272 | 0.125 | 110 | 29920
p66 | 0.05 | 280 | 0.15 | 135 | 37800
p67 | 0.05 | 282 | 0.125 | 110 | 31020
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e08
This sheet contains the results for tank connected to node: e08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.47 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | b12
Cost: | €175.91 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1172.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.48 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.48 | m above nearest node |  | Tank Cost | €646,017.16
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,593,189.00
|  |  |  | Total Investment Cost | €3,146,711.49
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p61 | 0.125 | 277 | 0.25 | 225 | 62325
p63 | 0.1 | 354 | 0.15 | 135 | 47790
p64 | 0.1 | 325 | 0.2 | 180 | 58500
p65 | 0.08 | 272 | 0.25 | 225 | 61200
p66 | 0.05 | 280 | 0.15 | 135 | 37800
p67 | 0.05 | 282 | 0.25 | 225 | 63450
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## f01
This sheet contains the results for tank connected to node: f01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.44 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €166.44 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1109.63 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.82 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.82 | m above nearest node |  | Tank Cost | €638,698.18
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,423,724.00
|  |  |  | Total Investment Cost | €2,969,927.51
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p53 | 0.1 | 177 | 0.125 | 110 | 19470
p54 | 0.08 | 177 | 0.125 | 110 | 19470
p55 | 0.08 | 159 | 0.125 | 110 | 17490
p56 | 0.1 | 349 | 0.125 | 110 | 38390
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p60 | 0.15 | 289 | 0.2 | 180 | 52020
p66 | 0.05 | 280 | 0.08 | 72 | 20160
p68 | 0.15 | 366 | 0.4 | 360 | 131760
p69 | 0.15 | 452 | 0.4 | 360 | 162720