## Summary
Summary of results for tank connected to each node
| Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
0 | J68 | 3 | 46.65 | 17.57 | 17.59 | 107.92 | 256.95 | 98.1 | 18.1 | 202.36 | 20.1 | 22 | J68 | [] | 220783.94 | 341339.47 | 0 | 562123.41 | 7146.39 | 49008.48 | 95544.8
1 | pump1 | 0 | 47.89 | 17.57 | 17.59 | 110.75 | 263.68 | 101.92 | 71.92 | 202.36 | 20.06 | 7 | J68 | [] | 220783.94 | 374013.57 | 0 | 594797.52 | 7407.79 | 51857.16 | 99687.12
1
[22 empty] | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc)
[22 empty] | J68 | 3 | 46.65 | 17.57 | 17.59 | 107.92 | 256.95 | 98.1 | 18.1 | 202.36 | 20.1
[22 empty] | pump1 | 0 | 47.89 | 17.57 | 17.59 | 110.75 | 263.68 | 101.92 | 71.92 | 202.36 | 20.06
[22 empty] | Node | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
[22 empty] | J68 | 22 | J68 | [] | 220783.94 | 341339.47 | 0 | 562123.41 | 7146.39 | 49008.48 | 95544.8
[22 empty] | pump1 | 7 | J68 | [] | 220783.94 | 374013.57 | 0 | 594797.52 | 7407.79 | 51857.16 | 99687.12

## J68
This sheet contains the results for tank connected to node: J68
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.65 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 17.57 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 17.59 | L/s |  | Critical Node | J68
Cost: | € 107.92 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 256.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 98.1 | m above sea level |  | Pump Cost | € 220,783.94
Tank height above ground | 18.1 | m above nearest node |  | Tank Cost | € 341,339.47
Tank volume | 202.36 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 562,123.41
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost

## pump1
This sheet contains the results for tank connected to node: pump1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 47.89 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 17.57 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 17.59 | L/s |  | Critical Node | J68
Cost: | € 110.75 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 263.68 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 101.92 | m above sea level |  | Pump Cost | € 220,783.94
Tank height above ground | 71.92 | m above nearest node |  | Tank Cost | € 374,013.57
Tank volume | 202.36 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 594,797.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost