## Sheet1
|  | Balancing volume: | 2318.2047 | MAX(F6:F29)+ABS(MIN(F6:F29)) | Start Volume | 8127.857 | 5954.555 |  | 5954.555
System Flow Balance |  | Total Volume | 10446.0617 |  |  | 794.74 |  |  |  | Original Balancing Volume
Average: | 0 | 724.434 |  |  | daily_demand | 17386.4163 |  |  |  | 2318.2047
| 48 | 724.434
Series | Time (hours) | Demand (CMH) | Pumped Flow | in - out | Cumulative | Volume |  | Rolling sum | 16400.6168 | Emergency volume
1 | 0 | 608.5198 | 724.434 | 115.9142 | 115.9142 | 8127.857 |  |  |  | 2173.3022
1 | 1 | 427.4127 | 724.434 | 297.0213 | 412.9355 | 8243.7712
1 | 2 | 115.9085 | 724.434 | 608.5255 | 1021.461 | 8540.7925 |  |  | 4491.5069
1 | 3 | 115.9085 | 724.434 | 608.5255 | 1629.9865 | 9149.318
1 | 4 | 289.7713 | 724.434 | 434.6627 | 2064.6493 | 9757.8435
1 | 5 | 470.8784 | 724.434 | 253.5556 | 2318.2049 | 10192.5063
1 | 6 | 782.3826 | 724.434 | -57.9486 | 2260.2563 | 10446.0619
1 | 7 | 996.089 | 724.434 | -271.655 | 1988.6013 | 10388.1133
1 | 8 | 1267.7496 | 724.434 | -543.3156 | 1445.2857 | 10116.4583
1 | 9 | 905.5354 | 724.434 | -181.1014 | 1264.1843 | 9573.1427
1 | 10 | 804.1155 | 724.434 | -79.6815 | 1184.5028 | 9392.0413
1 | 11 | 869.314 | 724.434 | -144.88 | 1039.6228 | 9312.3598
1 | 12 | 905.5354 | 724.434 | -181.1014 | 858.5215 | 9167.4798
1 | 13 | 927.2683 | 724.434 | -202.8343 | 655.6872 | 8986.3785
1 | 14 | 870.8694 | 724.434 | -146.4354 | 509.2518 | 8783.5442
1 | 15 | 746.4592 | 724.434 | -22.0252 | 487.2266 | 8637.1088
1 | 16 | 746.4592 | 724.434 | -22.0252 | 465.2014 | 8615.0836
1 | 17 | 622.0494 | 724.434 | 102.3846 | 567.586 | 8593.0584
1 | 18 | 622.0494 | 724.434 | 102.3846 | 669.9706 | 8695.443
1 | 19 | 808.6642 | 724.434 | -84.2302 | 585.7404 | 8797.8276
1 | 20 | 933.0741 | 724.434 | -208.6401 | 377.1004 | 8713.5974
1 | 21 | 933.0741 | 0 | -933.0741 | -555.9737 | 8504.9574
1 | 22 | 870.8691 | 0 | -870.8691 | -1426.8428 | 7571.8833
1 | 23 | 746.4592 | 0 | -746.4592 | -2173.302 | 6701.0142
1 | 24 | 608.5198 | 833.0991 | 224.5793 | -1948.7227 | 5954.555 |  | 15213.1143
2 | 25 | 608.5198 | 833.0991 | 224.5793 | -1724.1434 | 5954.555 |  | 15321.7794
2 | 26 | 427.4127 | 833.0991 | 405.6864 | -1318.457 | 6179.1343 |  | 15430.4445
2 | 27 | 115.9085 | 833.0991 | 717.1906 | -601.2664 | 6584.8207 |  | 15539.1096
2 | 28 | 115.9085 | 833.0991 | 717.1906 | 115.9242 | 7302.0113 |  | 15647.7747
2 | 29 | 289.7713 | 833.0991 | 543.3278 | 659.252 | 8019.2019 |  | 15756.4398
2 | 30 | 470.8784 | 833.0991 | 362.2207 | 1021.4728 | 8562.5297 |  | 15865.1049
2 | 31 | 782.3826 | 833.0991 | 50.7165 | 1072.1893 | 8924.7504 |  | 15973.77
2 | 32 | 996.089 | 833.0991 | -162.9899 | 909.1994 | 8975.467 |  | 16082.4351
2 | 33 | 1267.7496 | 833.0991 | -434.6505 | 474.5489 | 8812.4771 |  | 16191.1002
2 | 34 | 905.5354 | 833.0991 | -72.4363 | 402.1126 | 8377.8266 |  | 16299.7653
2 | 35 | 804.1155 | 833.0991 | 28.9836 | 431.0962 | 8305.3903 |  | 16408.4304
2 | 36 | 869.314 | 833.0991 | -36.2149 | 394.8813 | 8334.3739 |  | 16517.0955
2 | 37 | 905.5354 | 833.0991 | -72.4363 | 322.4451 | 8298.159 |  | 16625.7606
2 | 38 | 927.2683 | 833.0991 | -94.1692 | 228.2759 | 8225.7227 |  | 16734.4257
2 | 39 | 870.8694 | 724.434 | -146.4354 | 81.8405 | 8131.5536 |  | 16843.0908
2 | 40 | 746.4592 | 724.434 | -22.0252 | 59.8153 | 7985.1182 |  | 16843.0908
2 | 41 | 746.4592 | 724.434 | -22.0252 | 37.7901 | 7963.093 |  | 16843.0908
2 | 42 | 622.0494 | 724.434 | 102.3846 | 140.1747 | 7941.0678 |  | 16843.0908
2 | 43 | 622.0494 | 724.434 | 102.3846 | 242.5593 | 8043.4524 |  | 16843.0908
2 | 44 | 808.6642 | 724.434 | -84.2302 | 158.3292 | 8145.837 |  | 16843.0908
2 | 45 | 933.0741 | 724.434 | -208.6401 | -50.3109 | 8061.6068 |  | 16843.0908
2 | 46 | 933.0741 | 724.434 | -208.6401 | -258.951 | 7852.9668 |  | 17567.5248
2 | 47 | 870.8691 | 724.434 | -146.4351 | -405.3861 | 7644.3267 |  | 18291.9588
2 | 48 | 746.4592 | 724.434 | -22.0252 | -427.4113 | 7497.8916 |  | 19016.3928
3 | 25 | 608.5198 | 724.434 | 115.9142 | -311.4971 | 7497.8916 |  | 18907.7277
3 | 26 | 427.4127 | 724.434 | 297.0213 | -14.4758 | 7613.8058 |  | 18799.0626
3 | 27 | 115.9085 | 724.434 | 608.5255 | 594.0497 | 7910.8271 |  | 18690.3975
3 | 28 | 115.9085 | 724.434 | 608.5255 | 1202.5753 | 8519.3526 |  | 18581.7324
3 | 29 | 289.7713 | 724.434 | 434.6627 | 1637.238 | 9127.8781 |  | 18473.0673
3 | 30 | 470.8784 | 724.434 | 253.5556 | 1890.7936 | 9562.5408 |  | 18364.4022
3 | 31 | 782.3826 | 724.434 | -57.9486 | 1832.845 | 9816.0965 |  | 18255.7371
3 | 32 | 996.089 | 724.434 | -271.655 | 1561.19 | 9758.1479 |  | 18147.072
3 | 33 | 1267.7496 | 724.434 | -543.3156 | 1017.8744 | 9486.4929 |  | 18038.4069
3 | 34 | 905.5354 | 724.434 | -181.1014 | 836.773 | 8943.1773 |  | 17929.7418
3 | 35 | 804.1155 | 724.434 | -79.6815 | 757.0915 | 8762.0759 |  | 17821.0767
3 | 36 | 869.314 | 724.434 | -144.88 | 612.2116 | 8682.3944 |  | 17712.4116
3 | 37 | 905.5354 | 724.434 | -181.1014 | 431.1102 | 8537.5144 |  | 17603.7465
3 | 38 | 927.2683 | 724.434 | -202.8343 | 228.2759 | 8356.413 |  | 17495.0814
3 | 39 | 870.8694 | 724.434 | -146.4354 | 81.8405 | 8153.5788 |  | 17386.4163
3 | 40 | 746.4592 | 724.434 | -22.0252 | 59.8153 | 8007.1434 |  | 17386.4163
3 | 41 | 746.4592 | 724.434 | -22.0252 | 37.7901 | 7985.1182 |  | 17386.4163
3 | 42 | 622.0494 | 724.434 | 102.3846 | 140.1747 | 7963.093 |  | 17386.4163
3 | 43 | 622.0494 | 724.434 | 102.3846 | 242.5593 | 8065.4776 |  | 17386.4163
3 | 44 | 808.6642 | 724.434 | -84.2302 | 158.3292 | 8167.8622 |  | 17386.4163
3 | 45 | 933.0741 | 724.434 | -208.6401 | -50.3109 | 8083.632 |  | 17386.4163
3 | 46 | 933.0741 | 724.434 | -208.6401 | -258.951 | 7874.9919 |  | 17386.4163
3 | 47 | 870.8691 | 724.434 | -146.4351 | -405.3861 | 7666.3519 |  | 17386.4163
3 | 48 | 746.4592 | 724.434 | -22.0252 | -427.4113 | 7519.9168 |  | 17386.4163
4 | 25 | 608.5198 | 724.434 | 115.9142 | -311.4971 | 7519.9168 |  | 17386.4163
4 | 26 | 427.4127 | 724.434 | 297.0213 | -14.4758 | 7635.831 |  | 17386.4163
4 | 27 | 115.9085 | 724.434 | 608.5255 | 594.0497 | 7932.8523 |  | 17386.4163
4 | 28 | 115.9085 | 724.434 | 608.5255 | 1202.5753 | 8541.3778 |  | 17386.4163
4 | 29 | 289.7713 | 724.434 | 434.6627 | 1637.238 | 9149.9033 |  | 17386.4163
4 | 30 | 470.8784 | 724.434 | 253.5556 | 1890.7936 | 9584.566 |  | 17386.4163
4 | 31 | 782.3826 | 724.434 | -57.9486 | 1832.845 | 9838.1216 |  | 17386.4163
4 | 32 | 996.089 | 724.434 | -271.655 | 1561.19 | 9780.1731 |  | 17386.4163
4 | 33 | 1267.7496 | 724.434 | -543.3156 | 1017.8744 | 9508.5181 |  | 17386.4163
4 | 34 | 905.5354 | 724.434 | -181.1014 | 836.773 | 8965.2025 |  | 17386.4163
4 | 35 | 804.1155 | 724.434 | -79.6815 | 757.0915 | 8784.1011 |  | 17386.4163
4 | 36 | 869.314 | 724.434 | -144.88 | 612.2116 | 8704.4196 |  | 17386.4163
4 | 37 | 905.5354 | 724.434 | -181.1014 | 431.1102 | 8559.5396 |  | 17386.4163
4 | 38 | 927.2683 | 724.434 | -202.8343 | 228.2759 | 8378.4382 |  | 17386.4163
4 | 39 | 870.8694 | 724.434 | -146.4354 | 81.8405 | 8175.6039 |  | 17386.4163
4 | 40 | 746.4592 | 724.434 | -22.0252 | 59.8153 | 8029.1686 |  | 17386.4163
4 | 41 | 746.4592 | 724.434 | -22.0252 | 37.7901 | 8007.1434 |  | 17386.4163
4 | 42 | 622.0494 | 724.434 | 102.3846 | 140.1747 | 7985.1182 |  | 17386.4163
4 | 43 | 622.0494 | 724.434 | 102.3846 | 242.5593 | 8087.5028 |  | 17386.4163
4 | 44 | 808.6642 | 724.434 | -84.2302 | 158.3292 | 8189.8874 |  | 17386.4163
4 | 45 | 933.0741 | 724.434 | -208.6401 | -50.3109 | 8105.6572 |  | 17386.4163
4 | 46 | 933.0741 | 724.434 | -208.6401 | -258.951 | 7897.0171 |  | 17386.4163
4 | 47 | 870.8691 | 724.434 | -146.4351 | -405.3861 | 7688.377 |  | 17386.4163
4 | 48 | 746.4592 | 724.434 | -22.0252 | -427.4113 | 7541.942 |  | 17386.4163
5 | 25 | 608.5198 | 724.434 | 115.9142 | -311.4971 | 7541.942 |  | 17386.4163
5 | 26 | 427.4127 | 724.434 | 297.0213 | -14.4758 | 7657.8562 |  | 17386.4163
5 | 27 | 115.9085 | 724.434 | 608.5255 | 594.0497 | 7954.8775 |  | 17386.4163
5 | 28 | 115.9085 | 724.434 | 608.5255 | 1202.5753 | 8563.403 |  | 17386.4163
5 | 29 | 289.7713 | 724.434 | 434.6627 | 1637.238 | 9171.9285 |  | 17386.4163
5 | 30 | 470.8784 | 724.434 | 253.5556 | 1890.7936 | 9606.5912 |  | 17386.4163
5 | 31 | 782.3826 | 724.434 | -57.9486 | 1832.845 | 9860.1468 |  | 17386.4163
5 | 32 | 996.089 | 724.434 | -271.655 | 1561.19 | 9802.1982 |  | 17386.4163
5 | 33 | 1267.7496 | 724.434 | -543.3156 | 1017.8744 | 9530.5433 |  | 17386.4163
5 | 34 | 905.5354 | 724.434 | -181.1014 | 836.773 | 8987.2277 |  | 17386.4163
5 | 35 | 804.1155 | 724.434 | -79.6815 | 757.0915 | 8806.1263 |  | 17386.4163
5 | 36 | 869.314 | 724.434 | -144.88 | 612.2116 | 8726.4448 |  | 17386.4163
5 | 37 | 905.5354 | 724.434 | -181.1014 | 431.1102 | 8581.5648 |  | 17386.4163
5 | 38 | 927.2683 | 724.434 | -202.8343 | 228.2759 | 8400.4634 |  | 17386.4163
5 | 39 | 870.8694 | 724.434 | -146.4354 | 81.8405 | 8197.6291 |  | 17386.4163
5 | 40 | 746.4592 | 724.434 | -22.0252 | 59.8153 | 8051.1937 |  | 17386.4163
5 | 41 | 746.4592 | 724.434 | -22.0252 | 37.7901 | 8029.1686 |  | 17386.4163
5 | 42 | 622.0494 | 724.434 | 102.3846 | 140.1747 | 8007.1434 |  | 17386.4163
5 | 43 | 622.0494 | 724.434 | 102.3846 | 242.5593 | 8109.528 |  | 17386.4163
5 | 44 | 808.6642 | 724.434 | -84.2302 | 158.3292 | 8211.9126 |  | 17386.4163
5 | 45 | 933.0741 | 724.434 | -208.6401 | -50.3109 | 8127.6824 |  | 17386.4163
5 | 46 | 933.0741 | 724.434 | -208.6401 | -258.951 | 7919.0423 |  | 17386.4163
5 | 47 | 870.8691 | 724.434 | -146.4351 | -405.3861 | 7710.4022 |  | 17386.4163
5 | 48 | 746.4592 | 724.434 | -22.0252 | -427.4113 | 7563.9671 |  | 17386.4163
6 | 25 | 608.5198 | 724.434 | 115.9142 | -311.4971 | 7563.9671 |  | 17386.4163
6 | 26 | 427.4127 | 724.434 | 297.0213 | -14.4758 | 7679.8814 |  | 17386.4163
6 | 27 | 115.9085 | 724.434 | 608.5255 | 594.0497 | 7976.9027 |  | 17386.4163
6 | 28 | 115.9085 | 724.434 | 608.5255 | 1202.5753 | 8585.4282 |  | 17386.4163
6 | 29 | 289.7713 | 724.434 | 434.6627 | 1637.238 | 9193.9537 |  | 17386.4163
6 | 30 | 470.8784 | 724.434 | 253.5556 | 1890.7936 | 9628.6164 |  | 17386.4163
6 | 31 | 782.3826 | 724.434 | -57.9486 | 1832.845 | 9882.172 |  | 17386.4163
6 | 32 | 996.089 | 724.434 | -271.655 | 1561.19 | 9824.2234 |  | 17386.4163
6 | 33 | 1267.7496 | 724.434 | -543.3156 | 1017.8744 | 9552.5684 |  | 17386.4163
6 | 34 | 905.5354 | 724.434 | -181.1014 | 836.773 | 9009.2529 |  | 17386.4163
6 | 35 | 804.1155 | 724.434 | -79.6815 | 757.0915 | 8828.1515 |  | 17386.4163
6 | 36 | 869.314 | 724.434 | -144.88 | 612.2116 | 8748.47 |  | 17386.4163
6 | 37 | 905.5354 | 724.434 | -181.1014 | 431.1102 | 8603.59 |  | 17386.4163
6 | 38 | 927.2683 | 724.434 | -202.8343 | 228.2759 | 8422.4886 |  | 17386.4163
6 | 39 | 870.8694 | 724.434 | -146.4354 | 81.8405 | 8219.6543 |  | 17386.4163
6 | 40 | 746.4592 | 724.434 | -22.0252 | 59.8153 | 8073.2189 |  | 17386.4163
6 | 41 | 746.4592 | 724.434 | -22.0252 | 37.7901 | 8051.1937 |  | 17386.4163
6 | 42 | 622.0494 | 724.434 | 102.3846 | 140.1747 | 8029.1686 |  | 17386.4163
6 | 43 | 622.0494 | 724.434 | 102.3846 | 242.5593 | 8131.5532 |  | 17386.4163
6 | 44 | 808.6642 | 724.434 | -84.2302 | 158.3292 | 8233.9378 |  | 17386.4163
6 | 45 | 933.0741 | 724.434 | -208.6401 | -50.3109 | 8149.7076 |  | 17386.4163
6 | 46 | 933.0741 | 724.434 | -208.6401 | -258.951 | 7941.0675 |  | 17386.4163
6 | 47 | 870.8691 | 724.434 | -146.4351 | -405.3861 | 7732.4274 |  | 17386.4163
6 | 48 | 746.4592 | 724.434 | -22.0252 | -427.4113 | 7585.9923 |  | 17386.4163
7 | 25 | 608.5198 | 724.434 | 115.9142 | -311.4971 | 7585.9923 |  | 17386.4163
7 | 26 | 427.4127 | 724.434 | 297.0213 | -14.4758 | 7701.9065 |  | 17386.4163
7 | 27 | 115.9085 | 724.434 | 608.5255 | 594.0497 | 7998.9279 |  | 17386.4163
7 | 28 | 115.9085 | 724.434 | 608.5255 | 1202.5753 | 8607.4534 |  | 17386.4163
7 | 29 | 289.7713 | 724.434 | 434.6627 | 1637.238 | 9215.9789 |  | 17386.4163
7 | 30 | 470.8784 | 724.434 | 253.5556 | 1890.7936 | 9650.6416 |  | 17386.4163
7 | 31 | 782.3826 | 724.434 | -57.9486 | 1832.845 | 9904.1972 |  | 17386.4163
7 | 32 | 996.089 | 724.434 | -271.655 | 1561.19 | 9846.2486 |  | 17386.4163
7 | 33 | 1267.7496 | 724.434 | -543.3156 | 1017.8744 | 9574.5936 |  | 17386.4163
7 | 34 | 905.5354 | 724.434 | -181.1014 | 836.773 | 9031.278 |  | 17386.4163
7 | 35 | 804.1155 | 724.434 | -79.6815 | 757.0915 | 8850.1767 |  | 17386.4163
7 | 36 | 869.314 | 724.434 | -144.88 | 612.2116 | 8770.4952 |  | 17386.4163
7 | 37 | 905.5354 | 724.434 | -181.1014 | 431.1102 | 8625.6152 |  | 17386.4163
7 | 38 | 927.2683 | 724.434 | -202.8343 | 228.2759 | 8444.5138 |  | 17386.4163
7 | 39 | 870.8694 | 724.434 | -146.4354 | 81.8405 | 8241.6795 |  | 17386.4163
7 | 40 | 746.4592 | 724.434 | -22.0252 | 59.8153 | 8095.2441 |  | 17386.4163
7 | 41 | 746.4592 | 724.434 | -22.0252 | 37.7901 | 8073.2189 |  | 17386.4163
7 | 42 | 622.0494 | 724.434 | 102.3846 | 140.1747 | 8051.1937 |  | 17386.4163
7 | 43 | 622.0494 | 724.434 | 102.3846 | 242.5593 | 8153.5784 |  | 17386.4163
7 | 44 | 808.6642 | 724.434 | -84.2302 | 158.3292 | 8255.963 |  | 17386.4163
7 | 45 | 933.0741 | 724.434 | -208.6401 | -50.3109 | 8171.7328 |  | 17386.4163
7 | 46 | 933.0741 | 724.434 | -208.6401 | -258.951 | 7963.0927 |  | 17386.4163
7 | 47 | 870.8691 | 724.434 | -146.4351 | -405.3861 | 7754.4526 |  | 17386.4163
7 | 48 | 746.4592 | 724.434 | -22.0252 | -427.4113 | 7608.0175 |  | 17386.4163

## Sheet4
| Power_Out_Start | Tank_Emerg_Vol
0 | 0 | -644.7492
1 | 1 | -1361.9397
2 | 2 | -1327.87
3 | 3 | -610.6794
4 | 4 | 106.5111
5 | 5 | 649.8389
6 | 6 | 1012.0596
7 | 7 | 1120.7247
8 | 8 | 1229.3898
9 | 9 | 1338.0549
10 | 10 | 1446.72
11 | 11 | 1555.3851
12 | 12 | 1664.0502
13 | 13 | 1686.0755
14 | 14 | 1708.1007
15 | 15 | 1607.9513
16 | 16 | 1716.6164
17 | 17 | 1825.2815
18 | 18 | 1933.9466
19 | 19 | 2042.6117
20 | 20 | 2151.2768
21 | 21 | 2173.302
22 | 22 | 1448.868
23 | 23 | 724.434
24 | 24 | 4.5475e-13

## Sheet3
| Power_Out_Start | Tank_Emerg_Vol |  | Power_Out_Start | Tank_Emerg_Vol
0 | 0 | 2948.4313 | 0 | 0 | 2948.4313 |  | Power_Out_Start | Tank_Emerg_Vol
1 | 1 | 2948.4313 | 1 | 1 | 2948.4313 | 0 | 0 | 2948.4313
2 | 2 | 2948.4313 | 2 | 2 | 2948.4313 | 1 | 1 | 2448.5709
3 | 3 | 2948.4313 | 3 | 3 | 2948.4313 | 2 | 2 | 2482.6684
4 | 4 | 2948.4313 | 4 | 4 | 2948.4313 | 3 | 3 | 1982.8081
5 | 5 | 2948.4313 | 5 | 5 | 2948.4313 | 4 | 4 | 1482.9477
6 | 6 | 2948.4313 | 6 | 6 | 2948.4313 | 5 | 5 | 1156.9501
7 | 7 | 2948.4313 | 7 | 7 | 2948.4313 | 6 | 6 | 1012.0596
8 | 8 | 2948.4313 | 8 | 8 | 2948.4313 | 7 | 7 | 1120.7247
9 | 9 | 2948.4313 | 9 | 9 | 2948.4313 | 8 | 8 | 1229.3898
10 | 10 | 2948.4313 | 10 | 10 | 2948.4313 | 9 | 9 | 1338.0549
11 | 11 | 2948.4313 | 11 | 11 | 2948.4313 | 10 | 10 | 1446.72
12 | 12 | 2948.4313 | 12 | 12 | 2948.4313 | 11 | 11 | 1555.3851
13 | 13 | 2948.4313 | 13 | 13 | 2948.4313 | 12 | 12 | 1664.0502
14 | 14 | 2948.4313 | 14 | 14 | 2948.4313 | 13 | 13 | 1686.0755
15 | 15 | 2948.4313 | 15 | 15 | 2948.4313 | 14 | 14 | 1708.1007
16 | 16 | 2948.4313 | 16 | 16 | 2948.4313 | 15 | 15 | 1607.9513
17 | 17 | 2948.4313 | 17 | 17 | 2948.4313 | 16 | 16 | 1716.6164
18 | 18 | 2948.4313 | 18 | 18 | 2948.4313 | 17 | 17 | 1825.2815
19 | 19 | 2948.4313 | 19 | 19 | 2948.4313 | 18 | 18 | 1933.9466
20 | 20 | 2948.4313 | 20 | 20 | 2948.4313 | 19 | 19 | 2042.6117
21 | 21 | 2948.4313 | 21 | 21 | 2948.4313 | 20 | 20 | 2151.2768
22 | 22 | 2948.4313 | 22 | 22 | 2948.4313 | 21 | 21 | 2173.302
23 | 23 | 2948.4313 | 23 | 23 | 2948.4313 | 22 | 22 | 1448.868
[6 empty] | 23 | 23 | 724.434
[6 empty] | 24 | 24 | 2.1991e-12

## Sheet5
| index | Demand | Pumped_Flow | In_-_Out | Cumulative_Sum | Tank_Volume_for_outage_at: 0 | Tank_Volume_for_outage_at: 1 | Tank_Volume_for_outage_at: 2 | Tank_Volume_for_outage_at: 3 | Tank_Volume_for_outage_at: 4 | Tank_Volume_for_outage_at: 5 | Tank_Volume_for_outage_at: 6 | Tank_Volume_for_outage_at: 7 | Tank_Volume_for_outage_at: 8 | Tank_Volume_for_outage_at: 9 | Tank_Volume_for_outage_at: 10 | Tank_Volume_for_outage_at: 11 | Tank_Volume_for_outage_at: 12 | Tank_Volume_for_outage_at: 13 | Tank_Volume_for_outage_at: 14 | Tank_Volume_for_outage_at: 15 | Tank_Volume_for_outage_at: 16 | Tank_Volume_for_outage_at: 17 | Tank_Volume_for_outage_at: 18 | Tank_Volume_for_outage_at: 19 | Tank_Volume_for_outage_at: 20 | Tank_Volume_for_outage_at: 21 | Tank_Volume_for_outage_at: 22 | Tank_Volume_for_outage_at: 23 | Tank_Volume_for_outage_at: 24
0 | 0 | 0.16903 | 0.20123 | 115.9142 | 115.9142 | 1151.841 | 543.3156 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1120.7247 | 1229.3898 | 1338.0549 | 1446.72 | 1555.3851 | 1664.0502 | 1686.0755 | 1708.1007 | 1607.9513 | 1716.6164 | 1825.2815 | 1933.9466 | 2042.6117 | 2151.2768 | 2173.302 | 2057.3878 | 1760.3665 | 1151.841
1 | 3600 | 0.11873 | 0.20123 | 297.0213 | 412.9355 | 543.3212 | 659.2298 | 693.3134 | 801.9785 | 910.6436 | 1019.3087 | 1127.9738 | 1236.6389 | 1345.304 | 1453.9691 | 1562.6342 | 1671.2993 | 1779.9644 | 1801.9897 | 1824.0149 | 1723.8655 | 1832.5306 | 1941.1957 | 2049.8608 | 2158.5259 | 2267.191 | 2289.2162 | 2173.302 | 1876.2807 | 1267.7553
2 | 7200 | 0.032197 | 0.20123 | 608.5255 | 1021.461 | 115.9085 | 231.8171 | 990.3347 | 1098.9998 | 1207.6649 | 1316.33 | 1424.9951 | 1533.6602 | 1642.3253 | 1750.9904 | 1859.6555 | 1968.3206 | 2076.9857 | 2099.011 | 2121.0362 | 2020.8868 | 2129.5519 | 2238.217 | 2346.8821 | 2455.5472 | 2564.2123 | 2586.2375 | 2470.3233 | 2173.302 | 1564.7766
3 | 10800 | 0.032197 | 0.20123 | 608.5255 | 1629.9865 | 1.5632e-13 | 115.9085 | 874.4262 | 1707.5253 | 1816.1904 | 1924.8555 | 2033.5206 | 2142.1857 | 2250.8508 | 2359.5159 | 2468.181 | 2576.8461 | 2685.5112 | 2707.5364 | 2729.5617 | 2629.4123 | 2738.0774 | 2846.7425 | 2955.4076 | 3064.0727 | 3172.7378 | 3194.763 | 3078.8488 | 2781.8275 | 2173.302
4 | 14400 | 0.080492 | 0.20123 | 434.6627 | 2064.6491 | 717.1906 | -2.8422e-14 | 758.5176 | 1591.6168 | 2424.7159 | 2533.381 | 2642.0461 | 2750.7112 | 2859.3763 | 2968.0414 | 3076.7065 | 3185.3716 | 3294.0367 | 3316.0619 | 3338.0872 | 3237.9378 | 3346.6029 | 3455.268 | 3563.9331 | 3672.5982 | 3781.2633 | 3803.2885 | 3687.3743 | 3390.353 | 2781.8275
5 | 18000 | 0.1308 | 0.20123 | 253.5556 | 2318.2047 | 1260.5184 | 543.3278 | 468.7463 | 1301.8454 | 2134.9445 | 2968.0437 | 3076.7088 | 3185.3739 | 3294.039 | 3402.7041 | 3511.3692 | 3620.0343 | 3728.6994 | 3750.7246 | 3772.7498 | 3672.6004 | 3781.2655 | 3889.9306 | 3998.5957 | 4107.2608 | 4215.9259 | 4237.9512 | 4122.037 | 3825.0157 | 3216.4902
6 | 21600 | 0.21733 | 0.20123 | -57.9486 | 2260.2562 | 1622.7391 | 905.5485 | 830.967 | 830.967 | 1664.0661 | 2497.1652 | 3330.2644 | 3438.9295 | 3547.5946 | 3656.2597 | 3764.9248 | 3873.5899 | 3982.255 | 4004.2802 | 4026.3054 | 3926.156 | 4034.8211 | 4143.4862 | 4252.1513 | 4360.8164 | 4469.4815 | 4491.5068 | 4375.5926 | 4078.5713 | 3470.0458
7 | 25200 | 0.27669 | 0.20123 | -271.6549 | 1988.6012 | 1673.4556 | 956.265 | 881.6835 | 881.6835 | 881.6835 | 1714.7826 | 2547.8818 | 3380.9809 | 3489.646 | 3598.3111 | 3706.9762 | 3815.6413 | 3924.3064 | 3946.3316 | 3968.3568 | 3868.2074 | 3976.8725 | 4085.5376 | 4194.2028 | 4302.8679 | 4411.533 | 4433.5582 | 4317.644 | 4020.6227 | 3412.0972
8 | 28800 | 0.35215 | 0.20123 | -543.3156 | 1445.2856 | 1510.4657 | 793.2751 | 718.6937 | 718.6937 | 718.6937 | 718.6937 | 1551.7928 | 2384.8919 | 3217.991 | 3326.6561 | 3435.3212 | 3543.9863 | 3652.6514 | 3674.6767 | 3696.7019 | 3596.5525 | 3705.2176 | 3813.8827 | 3922.5478 | 4031.2129 | 4139.878 | 4161.9032 | 4045.989 | 3748.9677 | 3140.4423
9 | 32400 | 0.25154 | 0.20123 | -181.1014 | 1264.1842 | 1075.8153 | 358.6247 | 284.0432 | 284.0432 | 284.0432 | 284.0432 | 284.0432 | 1117.1423 | 1950.2414 | 2783.3406 | 2892.0057 | 3000.6708 | 3109.3359 | 3131.3611 | 3153.3863 | 3053.2369 | 3161.902 | 3270.5671 | 3379.2322 | 3487.8973 | 3596.5624 | 3618.5877 | 3502.6735 | 3205.6522 | 2597.1267
10 | 36000 | 0.22337 | 0.20123 | -79.6814 | 1184.5028 | 1003.379 | 286.1884 | 211.6069 | 211.6069 | 211.6069 | 211.6069 | 211.6069 | 211.6069 | 1044.706 | 1877.8051 | 2710.9043 | 2819.5694 | 2928.2345 | 2950.2597 | 2972.2849 | 2872.1355 | 2980.8006 | 3089.4657 | 3198.1308 | 3306.7959 | 3415.461 | 3437.4863 | 3321.5721 | 3024.5508 | 2416.0253
11 | 39600 | 0.24148 | 0.20123 | -144.88 | 1039.6228 | 1032.3626 | 315.172 | 240.5906 | 240.5906 | 240.5906 | 240.5906 | 240.5906 | 240.5906 | 240.5906 | 1073.6897 | 1906.7888 | 2739.8879 | 2848.553 | 2870.5783 | 2892.6035 | 2792.4541 | 2901.1192 | 3009.7843 | 3118.4494 | 3227.1145 | 3335.7796 | 3357.8048 | 3241.8906 | 2944.8693 | 2336.3438
12 | 43200 | 0.25154 | 0.20123 | -181.1014 | 858.5214 | 996.1477 | 278.9572 | 204.3757 | 204.3757 | 204.3757 | 204.3757 | 204.3757 | 204.3757 | 204.3757 | 204.3757 | 1037.4748 | 1870.5739 | 2703.673 | 2725.6983 | 2747.7235 | 2647.5741 | 2756.2392 | 2864.9043 | 2973.5694 | 3082.2345 | 3190.8996 | 3212.9248 | 3097.0106 | 2799.9893 | 2191.4639
13 | 46800 | 0.25757 | 0.20123 | -202.8343 | 655.6871 | 923.7114 | 206.5209 | 131.9394 | 131.9394 | 131.9394 | 131.9394 | 131.9394 | 131.9394 | 131.9394 | 131.9394 | 131.9394 | 965.0385 | 1798.1376 | 2544.5969 | 2566.6221 | 2466.4727 | 2575.1378 | 2683.8029 | 2792.468 | 2901.1331 | 3009.7982 | 3031.8234 | 2915.9092 | 2618.8879 | 2010.3625
14 | 50400 | 0.24191 | 0.20123 | -146.4353 | 509.2518 | 829.5423 | 112.3517 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 37.7702 | 870.8693 | 1617.3286 | 2363.7878 | 2263.6384 | 2372.3035 | 2480.9686 | 2589.6337 | 2698.2988 | 2806.964 | 2828.9892 | 2713.075 | 2416.0537 | 1807.5282
15 | 54000 | 0.20735 | 0.20123 | -22.0252 | 487.2266 | 791.772 | 74.5815 | -1.5632e-13 | 7.1054e-14 | -3.8369e-13 | -3.8369e-13 | -1.5632e-13 | 3.5527e-13 | -9.9476e-14 | -3.8369e-13 | 6.9633e-13 | 2.7001e-13 | -1.1369e-13 | 746.4592 | 1492.9185 | 2117.2031 | 2225.8682 | 2334.5333 | 2443.1984 | 2551.8635 | 2660.5286 | 2682.5539 | 2566.6396 | 2269.6183 | 1661.0929
16 | 57600 | 0.20735 | 0.20123 | -22.0252 | 465.2013 | 878.4119 | 161.2213 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | -3.4106e-13 | 746.4592 | 1370.7439 | 2203.843 | 2312.5081 | 2421.1732 | 2529.8383 | 2638.5034 | 2660.5286 | 2544.6144 | 2247.5931 | 1639.0676
17 | 61200 | 0.17279 | 0.20123 | 102.3846 | 567.586 | 965.0518 | 247.8612 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 173.2797 | 86.6399 | 0 | 624.2846 | 1457.3837 | 2290.4828 | 2399.1479 | 2507.813 | 2616.4781 | 2638.5034 | 2522.5892 | 2225.5679 | 1617.0424
18 | 64800 | 0.17279 | 0.20123 | 102.3846 | 669.9706 | 1176.1015 | 458.9109 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 384.3295 | 297.6896 | 211.0497 | 2.2352 | 835.3343 | 1668.4335 | 2501.5326 | 2610.1977 | 2718.8628 | 2740.888 | 2624.9738 | 2327.9525 | 1719.427
19 | 68400 | 0.22463 | 0.20123 | -84.2302 | 585.7404 | 1387.1513 | 669.9607 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 595.3792 | 508.7393 | 422.0995 | 213.285 | 213.285 | 1046.3841 | 1879.4832 | 2712.5823 | 2821.2474 | 2843.2727 | 2727.3584 | 2430.3371 | 1821.8117
20 | 72000 | 0.25919 | 0.20123 | -208.64 | 377.1004 | 1411.5862 | 694.3956 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 619.8141 | 533.1743 | 446.5344 | 237.7199 | 237.7199 | 237.7199 | 1070.819 | 1903.9181 | 2737.0172 | 2759.0425 | 2643.1283 | 2346.107 | 1737.5815
21 | 75600 | 0.25919 | 0.20123 | -208.64 | 168.4603 | 1311.6112 | 594.4207 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 519.8392 | 433.1993 | 346.5595 | 137.745 | 137.745 | 137.745 | 137.745 | 970.8441 | 1803.9432 | 2550.4024 | 2434.4882 | 2137.4669 | 1528.9414
22 | 79200 | 0.24191 | 0.20123 | -146.4351 | 22.0252 | 1211.6363 | 494.4457 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 419.8642 | 333.2244 | 246.5845 | 37.77 | 37.77 | 37.77 | 37.77 | 37.77 | 870.8691 | 1617.3284 | 2225.8482 | 1928.8269 | 1320.3014
23 | 82800 | 0.20735 | 0.20123 | -22.0252 | 1.2896e-12 | 1173.8663 | 456.6757 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 382.0942 | 295.4544 | 208.8145 | -7.816e-14 | -3.6238e-13 | -8.1712e-13 | -6.1817e-13 | -7.816e-14 | 0 | 746.4592 | 1354.979 | 1782.3918 | 1173.8663
24 | 86400 | 0.16903 | 0 | -608.5198 | -608.5198 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 382.0942 | 295.4544 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 86.6399 | 3.4106e-13 | 608.5198 | 1035.9325 | 1151.841
25 | 90000 | 0.11873 | 0 | -427.4127 | -1035.9325 | 1376.4204 | 659.2298 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 693.3134 | 693.3134 | 693.3134 | 693.3134 | 693.3134 | 606.6736 | 520.0337 | 311.2192 | 311.2192 | 311.2192 | 311.2192 | 311.2192 | 311.2192 | 224.5793 | 0 | 427.4127 | 543.3212
26 | 93600 | 0.032197 | 0 | -115.9085 | -1151.841 | 1673.4417 | 956.2511 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 990.3347 | 1098.9998 | 1098.9998 | 1098.9998 | 1098.9998 | 1012.3599 | 925.7201 | 716.9056 | 716.9056 | 716.9056 | 716.9056 | 716.9056 | 716.9056 | 630.2657 | 405.6864 | -7.9581e-13 | 115.9085
27 | 97200 | 0.032197 | 0.23142 | 717.1906 | -434.6505 | 2281.9671 | 1564.7766 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1598.8602 | 1707.5253 | 1816.1904 | 1816.1904 | 1816.1904 | 1729.5505 | 1642.9107 | 1434.0962 | 1434.0962 | 1434.0962 | 1434.0962 | 1434.0962 | 1434.0962 | 1347.4563 | 1122.877 | 717.1906 | -7.1054e-14
28 | 100800 | 0.080492 | 0.23142 | 543.3278 | 108.6773 | 2890.4926 | 2173.302 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2207.3857 | 2316.0508 | 2424.7159 | 2533.381 | 2533.381 | 2446.7411 | 2360.1012 | 2151.2867 | 2151.2867 | 2151.2867 | 2151.2867 | 2151.2867 | 2151.2867 | 2064.6469 | 1840.0676 | 1434.3812 | 717.1906
29 | 104400 | 0.1308 | 0.23142 | 362.2207 | 470.898 | 3325.1553 | 2607.9647 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2642.0484 | 2750.7135 | 2859.3786 | 2968.0437 | 3076.7088 | 2990.0689 | 2903.429 | 2694.6145 | 2694.6145 | 2694.6145 | 2694.6145 | 2694.6145 | 2694.6145 | 2607.9747 | 2383.3953 | 1977.7089 | 1260.5184
30 | 108000 | 0.21733 | 0.23142 | 50.7165 | 521.6145 | 3578.7109 | 2861.5203 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2895.6039 | 3004.269 | 3112.9341 | 3221.5993 | 3330.2644 | 3352.2896 | 3265.6497 | 3056.8352 | 3056.8352 | 3056.8352 | 3056.8352 | 3056.8352 | 3056.8352 | 2970.1954 | 2745.616 | 2339.9296 | 1622.7391
31 | 111600 | 0.27669 | 0.23142 | -162.9898 | 358.6247 | 3520.7623 | 2803.5717 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2837.6554 | 2946.3205 | 3054.9856 | 3163.6507 | 3272.3158 | 3294.341 | 3316.3662 | 3107.5517 | 3107.5517 | 3107.5517 | 3107.5517 | 3107.5517 | 3107.5517 | 3020.9119 | 2796.3326 | 2390.6462 | 1673.4556
32 | 115200 | 0.35215 | 0.23142 | -434.6505 | -76.0258 | 3249.1074 | 2531.9168 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2566.0004 | 2674.6655 | 2783.3306 | 2891.9957 | 3000.6608 | 3022.6861 | 3044.7113 | 2944.5619 | 2944.5619 | 2944.5619 | 2944.5619 | 2944.5619 | 2944.5619 | 2857.922 | 2633.3427 | 2227.6563 | 1510.4657
33 | 118800 | 0.25154 | 0.23142 | -72.4363 | -148.4621 | 2705.7918 | 1988.6012 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 2022.6848 | 2131.3499 | 2240.015 | 2348.6801 | 2457.3452 | 2479.3705 | 2501.3957 | 2401.2463 | 2509.9114 | 2509.9114 | 2509.9114 | 2509.9114 | 2509.9114 | 2423.2716 | 2198.6922 | 1793.0058 | 1075.8153
34 | 122400 | 0.22337 | 0.23142 | 28.9837 | -119.4784 | 2524.6904 | 1807.4998 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1841.5834 | 1950.2485 | 2058.9136 | 2167.5787 | 2276.2438 | 2298.2691 | 2320.2943 | 2220.1449 | 2328.81 | 2437.4751 | 2437.4751 | 2437.4751 | 2437.4751 | 2350.8353 | 2126.2559 | 1720.5695 | 1003.379
35 | 126000 | 0.24148 | 0.23142 | -36.2149 | -155.6933 | 2445.0089 | 1727.8184 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1761.902 | 1870.5671 | 1979.2322 | 2087.8973 | 2196.5624 | 2218.5876 | 2240.6129 | 2140.4635 | 2249.1286 | 2357.7937 | 2466.4588 | 2466.4588 | 2466.4588 | 2379.8189 | 2155.2396 | 1749.5532 | 1032.3626
36 | 129600 | 0.25154 | 0.23142 | -72.4363 | -228.1296 | 2300.129 | 1582.9384 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1617.022 | 1725.6871 | 1834.3522 | 1943.0173 | 2051.6824 | 2073.7077 | 2095.7329 | 1995.5835 | 2104.2486 | 2212.9137 | 2321.5788 | 2430.2439 | 2430.2439 | 2343.604 | 2119.0247 | 1713.3383 | 996.1477
37 | 133200 | 0.25757 | 0.23142 | -94.1692 | -322.2988 | 2119.0276 | 1401.837 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1435.9206 | 1544.5857 | 1653.2508 | 1761.9159 | 1870.581 | 1892.6063 | 1914.6315 | 1814.4821 | 1923.1472 | 2031.8123 | 2140.4774 | 2249.1425 | 2357.8076 | 2271.1677 | 2046.5884 | 1640.902 | 923.7114
38 | 136800 | 0.24191 | 0.23142 | -37.7702 | -360.069 | 1916.1933 | 1199.0027 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1233.0864 | 1341.7515 | 1450.4166 | 1559.0817 | 1667.7468 | 1689.772 | 1711.7972 | 1611.6478 | 1720.3129 | 1828.978 | 1937.6431 | 2046.3082 | 2154.9733 | 2176.9986 | 1952.4193 | 1546.7329 | 829.5423
39 | 140400 | 0.20735 | 0.23142 | 86.6399 | -273.4291 | 1769.758 | 1052.5674 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1565.3619 | 1465.2125 | 1573.8776 | 1682.5427 | 1791.2078 | 1899.8729 | 2008.538 | 2030.5632 | 1914.649 | 1508.9626 | 791.772
40 | 144000 | 0.20735 | 0.23142 | 86.6399 | -186.7893 | 1747.7327 | 1030.5421 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1543.3367 | 1443.1873 | 1551.8524 | 1660.5175 | 1769.1826 | 1877.8477 | 1986.5128 | 2008.538 | 1892.6238 | 1595.6025 | 878.4119
41 | 147600 | 0.17279 | 0.20123 | 102.3846 | -84.4046 | 1725.7075 | 1008.5169 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 1042.6005 | 1151.2656 | 1259.9307 | 1368.5959 | 1477.261 | 1499.2862 | 1521.3114 | 1421.162 | 1529.8271 | 1638.4922 | 1747.1573 | 1855.8224 | 1964.4875 | 1986.5128 | 1870.5986 | 1573.5773 | 965.0518
42 | 151200 | 0.17279 | 0.20123 | 102.3846 | 17.98 | 1828.0921 | 1110.9016 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1144.9852 | 1253.6503 | 1362.3154 | 1470.9805 | 1579.6456 | 1601.6708 | 1623.6961 | 1523.5467 | 1632.2118 | 1740.8769 | 1849.542 | 1958.2071 | 2066.8722 | 2088.8974 | 1972.9832 | 1675.9619 | 1067.4364
43 | 154800 | 0.22463 | 0.20123 | -84.2302 | -66.2502 | 1930.4768 | 1213.2862 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1247.3698 | 1356.0349 | 1464.7 | 1573.3651 | 1682.0302 | 1704.0555 | 1726.0807 | 1625.9313 | 1734.5964 | 1843.2615 | 1951.9266 | 2060.5917 | 2169.2568 | 2191.282 | 2075.3678 | 1778.3465 | 1169.8211
44 | 158400 | 0.25919 | 0.20123 | -208.64 | -274.8902 | 1846.2466 | 1129.056 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1163.1396 | 1271.8048 | 1380.4699 | 1489.135 | 1597.8001 | 1619.8253 | 1641.8505 | 1541.7011 | 1650.3662 | 1759.0313 | 1867.6964 | 1976.3615 | 2085.0266 | 2107.0519 | 1991.1377 | 1694.1164 | 1085.5909
45 | 162000 | 0.25919 | 0.20123 | -208.64 | -483.5303 | 1637.6065 | 920.416 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 954.4996 | 1063.1647 | 1171.8298 | 1280.4949 | 1389.16 | 1411.1852 | 1433.2105 | 1333.0611 | 1441.7262 | 1550.3913 | 1659.0564 | 1767.7215 | 1876.3866 | 1898.4118 | 1782.4976 | 1485.4763 | 876.9508
46 | 165600 | 0.24191 | 0.20123 | -146.4351 | -629.9654 | 1428.9665 | 711.7759 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 745.8596 | 854.5247 | 963.1898 | 1071.8549 | 1180.52 | 1202.5452 | 1224.5704 | 1124.421 | 1233.0861 | 1341.7512 | 1450.4163 | 1559.0814 | 1667.7465 | 1689.7718 | 1573.8576 | 1276.8363 | 668.3108
47 | 169200 | 0.20735 | 0.20123 | -22.0252 | -651.9906 | 1282.5314 | 565.3408 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 599.4244 | 708.0895 | 816.7546 | 925.4197 | 1034.0848 | 1056.1101 | 1078.1353 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1427.4224 | 1130.4012 | 521.8757
48 | 172800 | 0.16903 | 0.20123 | 115.9142 | -536.0764 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1034.0848 | 1056.1101 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1405.3972 | 1108.3759 | 499.8504
49 | 176400 | 0.11873 | 0.20123 | 297.0213 | -239.0551 | 1376.4204 | 659.2298 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 693.3134 | 801.9785 | 910.6436 | 1019.3087 | 1127.9738 | 1149.9991 | 1172.0243 | 1071.8749 | 1180.54 | 1289.2051 | 1397.8702 | 1506.5353 | 1615.2004 | 1637.2256 | 1521.3114 | 1224.2901 | 615.7647
50 | 180000 | 0.032197 | 0.20123 | 608.5255 | 369.4704 | 1673.4417 | 956.2511 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 990.3347 | 1098.9998 | 1207.6649 | 1316.33 | 1424.9951 | 1447.0204 | 1469.0456 | 1368.8962 | 1477.5613 | 1586.2264 | 1694.8915 | 1803.5566 | 1912.2217 | 1934.2469 | 1818.3327 | 1521.3114 | 912.7859
51 | 183600 | 0.032197 | 0.20123 | 608.5255 | 977.9959 | 2281.9671 | 1564.7766 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1598.8602 | 1707.5253 | 1816.1904 | 1924.8555 | 2033.5206 | 2055.5458 | 2077.5711 | 1977.4217 | 2086.0868 | 2194.7519 | 2303.417 | 2412.0821 | 2520.7472 | 2542.7724 | 2426.8582 | 2129.8369 | 1521.3114
52 | 187200 | 0.080492 | 0.20123 | 434.6627 | 1412.6585 | 2890.4926 | 2173.302 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2207.3857 | 2316.0508 | 2424.7159 | 2533.381 | 2642.0461 | 2664.0713 | 2686.0966 | 2585.9471 | 2694.6122 | 2803.2774 | 2911.9425 | 3020.6076 | 3129.2727 | 3151.2979 | 3035.3837 | 2738.3624 | 2129.8369
53 | 190800 | 0.1308 | 0.20123 | 253.5556 | 1666.2141 | 3325.1553 | 2607.9647 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2642.0484 | 2750.7135 | 2859.3786 | 2968.0437 | 3076.7088 | 3098.734 | 3120.7592 | 3020.6098 | 3129.2749 | 3237.94 | 3346.6051 | 3455.2702 | 3563.9353 | 3585.9606 | 3470.0464 | 3173.0251 | 2564.4996
54 | 194400 | 0.21733 | 0.20123 | -57.9486 | 1608.2655 | 3578.7109 | 2861.5203 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2895.6039 | 3004.269 | 3112.9341 | 3221.5993 | 3330.2644 | 3352.2896 | 3374.3148 | 3274.1654 | 3382.8305 | 3491.4956 | 3600.1607 | 3708.8258 | 3817.4909 | 3839.5162 | 3723.602 | 3426.5807 | 2818.0552
55 | 198000 | 0.27669 | 0.20123 | -271.6549 | 1336.6106 | 3520.7623 | 2803.5717 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2837.6554 | 2946.3205 | 3054.9856 | 3163.6507 | 3272.3158 | 3294.341 | 3316.3662 | 3216.2168 | 3324.8819 | 3433.547 | 3542.2121 | 3650.8772 | 3759.5423 | 3781.5676 | 3665.6534 | 3368.6321 | 2760.1066
56 | 201600 | 0.35215 | 0.20123 | -543.3156 | 793.295 | 3249.1074 | 2531.9168 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2566.0004 | 2674.6655 | 2783.3306 | 2891.9957 | 3000.6608 | 3022.6861 | 3044.7113 | 2944.5619 | 3053.227 | 3161.8921 | 3270.5572 | 3379.2223 | 3487.8874 | 3509.9126 | 3393.9984 | 3096.9771 | 2488.4516
57 | 205200 | 0.25154 | 0.20123 | -181.1014 | 612.1936 | 2705.7918 | 1988.6012 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 2022.6848 | 2131.3499 | 2240.015 | 2348.6801 | 2457.3452 | 2479.3705 | 2501.3957 | 2401.2463 | 2509.9114 | 2618.5765 | 2727.2416 | 2835.9067 | 2944.5718 | 2966.5971 | 2850.6829 | 2553.6616 | 1945.1361
58 | 208800 | 0.22337 | 0.20123 | -79.6814 | 532.5122 | 2524.6904 | 1807.4998 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1841.5834 | 1950.2485 | 2058.9136 | 2167.5787 | 2276.2438 | 2298.2691 | 2320.2943 | 2220.1449 | 2328.81 | 2437.4751 | 2546.1402 | 2654.8053 | 2763.4704 | 2785.4957 | 2669.5814 | 2372.5602 | 1764.0347
59 | 212400 | 0.24148 | 0.20123 | -144.88 | 387.6322 | 2445.0089 | 1727.8184 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1761.902 | 1870.5671 | 1979.2322 | 2087.8973 | 2196.5624 | 2218.5876 | 2240.6129 | 2140.4635 | 2249.1286 | 2357.7937 | 2466.4588 | 2575.1239 | 2683.789 | 2705.8142 | 2589.9 | 2292.8787 | 1684.3532
60 | 216000 | 0.25154 | 0.20123 | -181.1014 | 206.5308 | 2300.129 | 1582.9384 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1617.022 | 1725.6871 | 1834.3522 | 1943.0173 | 2051.6824 | 2073.7077 | 2095.7329 | 1995.5835 | 2104.2486 | 2212.9137 | 2321.5788 | 2430.2439 | 2538.909 | 2560.9342 | 2445.02 | 2147.9987 | 1539.4732
61 | 219600 | 0.25757 | 0.20123 | -202.8343 | 3.6965 | 2119.0276 | 1401.837 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1435.9206 | 1544.5857 | 1653.2508 | 1761.9159 | 1870.581 | 1892.6063 | 1914.6315 | 1814.4821 | 1923.1472 | 2031.8123 | 2140.4774 | 2249.1425 | 2357.8076 | 2379.8328 | 2263.9186 | 1966.8973 | 1358.3718
62 | 223200 | 0.24191 | 0.20123 | -146.4353 | -142.7388 | 1916.1933 | 1199.0027 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1233.0864 | 1341.7515 | 1450.4166 | 1559.0817 | 1667.7468 | 1689.772 | 1711.7972 | 1611.6478 | 1720.3129 | 1828.978 | 1937.6431 | 2046.3082 | 2154.9733 | 2176.9986 | 2061.0844 | 1764.0631 | 1155.5376
63 | 226800 | 0.20735 | 0.20123 | -22.0252 | -164.764 | 1769.758 | 1052.5674 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1565.3619 | 1465.2125 | 1573.8776 | 1682.5427 | 1791.2078 | 1899.8729 | 2008.538 | 2030.5632 | 1914.649 | 1617.6277 | 1009.1023
64 | 230400 | 0.20735 | 0.20123 | -22.0252 | -186.7893 | 1747.7327 | 1030.5421 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1543.3367 | 1443.1873 | 1551.8524 | 1660.5175 | 1769.1826 | 1877.8477 | 1986.5128 | 2008.538 | 1892.6238 | 1595.6025 | 987.077
65 | 234000 | 0.17279 | 0.20123 | 102.3846 | -84.4046 | 1725.7075 | 1008.5169 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 1042.6005 | 1151.2656 | 1259.9307 | 1368.5959 | 1477.261 | 1499.2862 | 1521.3114 | 1421.162 | 1529.8271 | 1638.4922 | 1747.1573 | 1855.8224 | 1964.4875 | 1986.5128 | 1870.5986 | 1573.5773 | 965.0518
66 | 237600 | 0.17279 | 0.20123 | 102.3846 | 17.98 | 1828.0921 | 1110.9016 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1144.9852 | 1253.6503 | 1362.3154 | 1470.9805 | 1579.6456 | 1601.6708 | 1623.6961 | 1523.5467 | 1632.2118 | 1740.8769 | 1849.542 | 1958.2071 | 2066.8722 | 2088.8974 | 1972.9832 | 1675.9619 | 1067.4364
67 | 241200 | 0.22463 | 0.20123 | -84.2302 | -66.2502 | 1930.4768 | 1213.2862 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1247.3698 | 1356.0349 | 1464.7 | 1573.3651 | 1682.0302 | 1704.0555 | 1726.0807 | 1625.9313 | 1734.5964 | 1843.2615 | 1951.9266 | 2060.5917 | 2169.2568 | 2191.282 | 2075.3678 | 1778.3465 | 1169.8211
68 | 244800 | 0.25919 | 0.20123 | -208.64 | -274.8902 | 1846.2466 | 1129.056 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1163.1396 | 1271.8048 | 1380.4699 | 1489.135 | 1597.8001 | 1619.8253 | 1641.8505 | 1541.7011 | 1650.3662 | 1759.0313 | 1867.6964 | 1976.3615 | 2085.0266 | 2107.0519 | 1991.1377 | 1694.1164 | 1085.5909
69 | 248400 | 0.25919 | 0.20123 | -208.64 | -483.5303 | 1637.6065 | 920.416 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 954.4996 | 1063.1647 | 1171.8298 | 1280.4949 | 1389.16 | 1411.1852 | 1433.2105 | 1333.0611 | 1441.7262 | 1550.3913 | 1659.0564 | 1767.7215 | 1876.3866 | 1898.4118 | 1782.4976 | 1485.4763 | 876.9508
70 | 252000 | 0.24191 | 0.20123 | -146.4351 | -629.9654 | 1428.9665 | 711.7759 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 745.8596 | 854.5247 | 963.1898 | 1071.8549 | 1180.52 | 1202.5452 | 1224.5704 | 1124.421 | 1233.0861 | 1341.7512 | 1450.4163 | 1559.0814 | 1667.7465 | 1689.7718 | 1573.8576 | 1276.8363 | 668.3108
71 | 255600 | 0.20735 | 0.20123 | -22.0252 | -651.9906 | 1282.5314 | 565.3408 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 599.4244 | 708.0895 | 816.7546 | 925.4197 | 1034.0848 | 1056.1101 | 1078.1353 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1427.4224 | 1130.4012 | 521.8757
72 | 259200 | 0.16903 | 0.20123 | 115.9142 | -536.0764 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1034.0848 | 1056.1101 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1405.3972 | 1108.3759 | 499.8504
73 | 262800 | 0.11873 | 0.20123 | 297.0213 | -239.0551 | 1376.4204 | 659.2298 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 693.3134 | 801.9785 | 910.6436 | 1019.3087 | 1127.9738 | 1149.9991 | 1172.0243 | 1071.8749 | 1180.54 | 1289.2051 | 1397.8702 | 1506.5353 | 1615.2004 | 1637.2256 | 1521.3114 | 1224.2901 | 615.7647
74 | 266400 | 0.032197 | 0.20123 | 608.5255 | 369.4704 | 1673.4417 | 956.2511 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 990.3347 | 1098.9998 | 1207.6649 | 1316.33 | 1424.9951 | 1447.0204 | 1469.0456 | 1368.8962 | 1477.5613 | 1586.2264 | 1694.8915 | 1803.5566 | 1912.2217 | 1934.2469 | 1818.3327 | 1521.3114 | 912.7859
75 | 270000 | 0.032197 | 0.20123 | 608.5255 | 977.9959 | 2281.9671 | 1564.7766 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1598.8602 | 1707.5253 | 1816.1904 | 1924.8555 | 2033.5206 | 2055.5458 | 2077.5711 | 1977.4217 | 2086.0868 | 2194.7519 | 2303.417 | 2412.0821 | 2520.7472 | 2542.7724 | 2426.8582 | 2129.8369 | 1521.3114
76 | 273600 | 0.080492 | 0.20123 | 434.6627 | 1412.6585 | 2890.4926 | 2173.302 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2207.3857 | 2316.0508 | 2424.7159 | 2533.381 | 2642.0461 | 2664.0713 | 2686.0966 | 2585.9471 | 2694.6122 | 2803.2774 | 2911.9425 | 3020.6076 | 3129.2727 | 3151.2979 | 3035.3837 | 2738.3624 | 2129.8369
77 | 277200 | 0.1308 | 0.20123 | 253.5556 | 1666.2141 | 3325.1553 | 2607.9647 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2642.0484 | 2750.7135 | 2859.3786 | 2968.0437 | 3076.7088 | 3098.734 | 3120.7592 | 3020.6098 | 3129.2749 | 3237.94 | 3346.6051 | 3455.2702 | 3563.9353 | 3585.9606 | 3470.0464 | 3173.0251 | 2564.4996
78 | 280800 | 0.21733 | 0.20123 | -57.9486 | 1608.2655 | 3578.7109 | 2861.5203 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2895.6039 | 3004.269 | 3112.9341 | 3221.5993 | 3330.2644 | 3352.2896 | 3374.3148 | 3274.1654 | 3382.8305 | 3491.4956 | 3600.1607 | 3708.8258 | 3817.4909 | 3839.5162 | 3723.602 | 3426.5807 | 2818.0552
79 | 284400 | 0.27669 | 0.20123 | -271.6549 | 1336.6106 | 3520.7623 | 2803.5717 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2837.6554 | 2946.3205 | 3054.9856 | 3163.6507 | 3272.3158 | 3294.341 | 3316.3662 | 3216.2168 | 3324.8819 | 3433.547 | 3542.2121 | 3650.8772 | 3759.5423 | 3781.5676 | 3665.6534 | 3368.6321 | 2760.1066
80 | 288000 | 0.35215 | 0.20123 | -543.3156 | 793.295 | 3249.1074 | 2531.9168 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2566.0004 | 2674.6655 | 2783.3306 | 2891.9957 | 3000.6608 | 3022.6861 | 3044.7113 | 2944.5619 | 3053.227 | 3161.8921 | 3270.5572 | 3379.2223 | 3487.8874 | 3509.9126 | 3393.9984 | 3096.9771 | 2488.4516
81 | 291600 | 0.25154 | 0.20123 | -181.1014 | 612.1936 | 2705.7918 | 1988.6012 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 2022.6848 | 2131.3499 | 2240.015 | 2348.6801 | 2457.3452 | 2479.3705 | 2501.3957 | 2401.2463 | 2509.9114 | 2618.5765 | 2727.2416 | 2835.9067 | 2944.5718 | 2966.5971 | 2850.6829 | 2553.6616 | 1945.1361
82 | 295200 | 0.22337 | 0.20123 | -79.6814 | 532.5122 | 2524.6904 | 1807.4998 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1841.5834 | 1950.2485 | 2058.9136 | 2167.5787 | 2276.2438 | 2298.2691 | 2320.2943 | 2220.1449 | 2328.81 | 2437.4751 | 2546.1402 | 2654.8053 | 2763.4704 | 2785.4957 | 2669.5814 | 2372.5602 | 1764.0347
83 | 298800 | 0.24148 | 0.20123 | -144.88 | 387.6322 | 2445.0089 | 1727.8184 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1761.902 | 1870.5671 | 1979.2322 | 2087.8973 | 2196.5624 | 2218.5876 | 2240.6129 | 2140.4635 | 2249.1286 | 2357.7937 | 2466.4588 | 2575.1239 | 2683.789 | 2705.8142 | 2589.9 | 2292.8787 | 1684.3532
84 | 302400 | 0.25154 | 0.20123 | -181.1014 | 206.5308 | 2300.129 | 1582.9384 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1617.022 | 1725.6871 | 1834.3522 | 1943.0173 | 2051.6824 | 2073.7077 | 2095.7329 | 1995.5835 | 2104.2486 | 2212.9137 | 2321.5788 | 2430.2439 | 2538.909 | 2560.9342 | 2445.02 | 2147.9987 | 1539.4732
85 | 306000 | 0.25757 | 0.20123 | -202.8343 | 3.6965 | 2119.0276 | 1401.837 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1435.9206 | 1544.5857 | 1653.2508 | 1761.9159 | 1870.581 | 1892.6063 | 1914.6315 | 1814.4821 | 1923.1472 | 2031.8123 | 2140.4774 | 2249.1425 | 2357.8076 | 2379.8328 | 2263.9186 | 1966.8973 | 1358.3718
86 | 309600 | 0.24191 | 0.20123 | -146.4353 | -142.7388 | 1916.1933 | 1199.0027 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1233.0864 | 1341.7515 | 1450.4166 | 1559.0817 | 1667.7468 | 1689.772 | 1711.7972 | 1611.6478 | 1720.3129 | 1828.978 | 1937.6431 | 2046.3082 | 2154.9733 | 2176.9986 | 2061.0844 | 1764.0631 | 1155.5376
87 | 313200 | 0.20735 | 0.20123 | -22.0252 | -164.764 | 1769.758 | 1052.5674 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1565.3619 | 1465.2125 | 1573.8776 | 1682.5427 | 1791.2078 | 1899.8729 | 2008.538 | 2030.5632 | 1914.649 | 1617.6277 | 1009.1023
88 | 316800 | 0.20735 | 0.20123 | -22.0252 | -186.7893 | 1747.7327 | 1030.5421 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1543.3367 | 1443.1873 | 1551.8524 | 1660.5175 | 1769.1826 | 1877.8477 | 1986.5128 | 2008.538 | 1892.6238 | 1595.6025 | 987.077
89 | 320400 | 0.17279 | 0.20123 | 102.3846 | -84.4046 | 1725.7075 | 1008.5169 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 1042.6005 | 1151.2656 | 1259.9307 | 1368.5959 | 1477.261 | 1499.2862 | 1521.3114 | 1421.162 | 1529.8271 | 1638.4922 | 1747.1573 | 1855.8224 | 1964.4875 | 1986.5128 | 1870.5986 | 1573.5773 | 965.0518
90 | 324000 | 0.17279 | 0.20123 | 102.3846 | 17.98 | 1828.0921 | 1110.9016 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1144.9852 | 1253.6503 | 1362.3154 | 1470.9805 | 1579.6456 | 1601.6708 | 1623.6961 | 1523.5467 | 1632.2118 | 1740.8769 | 1849.542 | 1958.2071 | 2066.8722 | 2088.8974 | 1972.9832 | 1675.9619 | 1067.4364
91 | 327600 | 0.22463 | 0.20123 | -84.2302 | -66.2502 | 1930.4768 | 1213.2862 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1247.3698 | 1356.0349 | 1464.7 | 1573.3651 | 1682.0302 | 1704.0555 | 1726.0807 | 1625.9313 | 1734.5964 | 1843.2615 | 1951.9266 | 2060.5917 | 2169.2568 | 2191.282 | 2075.3678 | 1778.3465 | 1169.8211
92 | 331200 | 0.25919 | 0.20123 | -208.64 | -274.8902 | 1846.2466 | 1129.056 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1163.1396 | 1271.8048 | 1380.4699 | 1489.135 | 1597.8001 | 1619.8253 | 1641.8505 | 1541.7011 | 1650.3662 | 1759.0313 | 1867.6964 | 1976.3615 | 2085.0266 | 2107.0519 | 1991.1377 | 1694.1164 | 1085.5909
93 | 334800 | 0.25919 | 0.20123 | -208.64 | -483.5303 | 1637.6065 | 920.416 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 954.4996 | 1063.1647 | 1171.8298 | 1280.4949 | 1389.16 | 1411.1852 | 1433.2105 | 1333.0611 | 1441.7262 | 1550.3913 | 1659.0564 | 1767.7215 | 1876.3866 | 1898.4118 | 1782.4976 | 1485.4763 | 876.9508
94 | 338400 | 0.24191 | 0.20123 | -146.4351 | -629.9654 | 1428.9665 | 711.7759 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 745.8596 | 854.5247 | 963.1898 | 1071.8549 | 1180.52 | 1202.5452 | 1224.5704 | 1124.421 | 1233.0861 | 1341.7512 | 1450.4163 | 1559.0814 | 1667.7465 | 1689.7718 | 1573.8576 | 1276.8363 | 668.3108
95 | 342000 | 0.20735 | 0.20123 | -22.0252 | -651.9906 | 1282.5314 | 565.3408 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 599.4244 | 708.0895 | 816.7546 | 925.4197 | 1034.0848 | 1056.1101 | 1078.1353 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1427.4224 | 1130.4012 | 521.8757
96 | 345600 | 0.16903 | 0.20123 | 115.9142 | -536.0764 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1034.0848 | 1056.1101 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1405.3972 | 1108.3759 | 499.8504
97 | 349200 | 0.11873 | 0.20123 | 297.0213 | -239.0551 | 1376.4204 | 659.2298 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 693.3134 | 801.9785 | 910.6436 | 1019.3087 | 1127.9738 | 1149.9991 | 1172.0243 | 1071.8749 | 1180.54 | 1289.2051 | 1397.8702 | 1506.5353 | 1615.2004 | 1637.2256 | 1521.3114 | 1224.2901 | 615.7647
98 | 352800 | 0.032197 | 0.20123 | 608.5255 | 369.4704 | 1673.4417 | 956.2511 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 990.3347 | 1098.9998 | 1207.6649 | 1316.33 | 1424.9951 | 1447.0204 | 1469.0456 | 1368.8962 | 1477.5613 | 1586.2264 | 1694.8915 | 1803.5566 | 1912.2217 | 1934.2469 | 1818.3327 | 1521.3114 | 912.7859
99 | 356400 | 0.032197 | 0.20123 | 608.5255 | 977.9959 | 2281.9671 | 1564.7766 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1598.8602 | 1707.5253 | 1816.1904 | 1924.8555 | 2033.5206 | 2055.5458 | 2077.5711 | 1977.4217 | 2086.0868 | 2194.7519 | 2303.417 | 2412.0821 | 2520.7472 | 2542.7724 | 2426.8582 | 2129.8369 | 1521.3114
100 | 360000 | 0.080492 | 0.20123 | 434.6627 | 1412.6585 | 2890.4926 | 2173.302 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2207.3857 | 2316.0508 | 2424.7159 | 2533.381 | 2642.0461 | 2664.0713 | 2686.0966 | 2585.9471 | 2694.6122 | 2803.2774 | 2911.9425 | 3020.6076 | 3129.2727 | 3151.2979 | 3035.3837 | 2738.3624 | 2129.8369
101 | 363600 | 0.1308 | 0.20123 | 253.5556 | 1666.2141 | 3325.1553 | 2607.9647 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2642.0484 | 2750.7135 | 2859.3786 | 2968.0437 | 3076.7088 | 3098.734 | 3120.7592 | 3020.6098 | 3129.2749 | 3237.94 | 3346.6051 | 3455.2702 | 3563.9353 | 3585.9606 | 3470.0464 | 3173.0251 | 2564.4996
102 | 367200 | 0.21733 | 0.20123 | -57.9486 | 1608.2655 | 3578.7109 | 2861.5203 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2895.6039 | 3004.269 | 3112.9341 | 3221.5993 | 3330.2644 | 3352.2896 | 3374.3148 | 3274.1654 | 3382.8305 | 3491.4956 | 3600.1607 | 3708.8258 | 3817.4909 | 3839.5162 | 3723.602 | 3426.5807 | 2818.0552
103 | 370800 | 0.27669 | 0.20123 | -271.6549 | 1336.6106 | 3520.7623 | 2803.5717 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2837.6554 | 2946.3205 | 3054.9856 | 3163.6507 | 3272.3158 | 3294.341 | 3316.3662 | 3216.2168 | 3324.8819 | 3433.547 | 3542.2121 | 3650.8772 | 3759.5423 | 3781.5676 | 3665.6534 | 3368.6321 | 2760.1066
104 | 374400 | 0.35215 | 0.20123 | -543.3156 | 793.295 | 3249.1074 | 2531.9168 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2566.0004 | 2674.6655 | 2783.3306 | 2891.9957 | 3000.6608 | 3022.6861 | 3044.7113 | 2944.5619 | 3053.227 | 3161.8921 | 3270.5572 | 3379.2223 | 3487.8874 | 3509.9126 | 3393.9984 | 3096.9771 | 2488.4516
105 | 378000 | 0.25154 | 0.20123 | -181.1014 | 612.1936 | 2705.7918 | 1988.6012 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 2022.6848 | 2131.3499 | 2240.015 | 2348.6801 | 2457.3452 | 2479.3705 | 2501.3957 | 2401.2463 | 2509.9114 | 2618.5765 | 2727.2416 | 2835.9067 | 2944.5718 | 2966.5971 | 2850.6829 | 2553.6616 | 1945.1361
106 | 381600 | 0.22337 | 0.20123 | -79.6814 | 532.5122 | 2524.6904 | 1807.4998 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1841.5834 | 1950.2485 | 2058.9136 | 2167.5787 | 2276.2438 | 2298.2691 | 2320.2943 | 2220.1449 | 2328.81 | 2437.4751 | 2546.1402 | 2654.8053 | 2763.4704 | 2785.4957 | 2669.5814 | 2372.5602 | 1764.0347
107 | 385200 | 0.24148 | 0.20123 | -144.88 | 387.6322 | 2445.0089 | 1727.8184 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1761.902 | 1870.5671 | 1979.2322 | 2087.8973 | 2196.5624 | 2218.5876 | 2240.6129 | 2140.4635 | 2249.1286 | 2357.7937 | 2466.4588 | 2575.1239 | 2683.789 | 2705.8142 | 2589.9 | 2292.8787 | 1684.3532
108 | 388800 | 0.25154 | 0.20123 | -181.1014 | 206.5308 | 2300.129 | 1582.9384 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1617.022 | 1725.6871 | 1834.3522 | 1943.0173 | 2051.6824 | 2073.7077 | 2095.7329 | 1995.5835 | 2104.2486 | 2212.9137 | 2321.5788 | 2430.2439 | 2538.909 | 2560.9342 | 2445.02 | 2147.9987 | 1539.4732
109 | 392400 | 0.25757 | 0.20123 | -202.8343 | 3.6965 | 2119.0276 | 1401.837 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1435.9206 | 1544.5857 | 1653.2508 | 1761.9159 | 1870.581 | 1892.6063 | 1914.6315 | 1814.4821 | 1923.1472 | 2031.8123 | 2140.4774 | 2249.1425 | 2357.8076 | 2379.8328 | 2263.9186 | 1966.8973 | 1358.3718
110 | 396000 | 0.24191 | 0.20123 | -146.4353 | -142.7388 | 1916.1933 | 1199.0027 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1233.0864 | 1341.7515 | 1450.4166 | 1559.0817 | 1667.7468 | 1689.772 | 1711.7972 | 1611.6478 | 1720.3129 | 1828.978 | 1937.6431 | 2046.3082 | 2154.9733 | 2176.9986 | 2061.0844 | 1764.0631 | 1155.5376
111 | 399600 | 0.20735 | 0.20123 | -22.0252 | -164.764 | 1769.758 | 1052.5674 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1565.3619 | 1465.2125 | 1573.8776 | 1682.5427 | 1791.2078 | 1899.8729 | 2008.538 | 2030.5632 | 1914.649 | 1617.6277 | 1009.1023
112 | 403200 | 0.20735 | 0.20123 | -22.0252 | -186.7893 | 1747.7327 | 1030.5421 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1543.3367 | 1443.1873 | 1551.8524 | 1660.5175 | 1769.1826 | 1877.8477 | 1986.5128 | 2008.538 | 1892.6238 | 1595.6025 | 987.077
113 | 406800 | 0.17279 | 0.20123 | 102.3846 | -84.4046 | 1725.7075 | 1008.5169 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 1042.6005 | 1151.2656 | 1259.9307 | 1368.5959 | 1477.261 | 1499.2862 | 1521.3114 | 1421.162 | 1529.8271 | 1638.4922 | 1747.1573 | 1855.8224 | 1964.4875 | 1986.5128 | 1870.5986 | 1573.5773 | 965.0518
114 | 410400 | 0.17279 | 0.20123 | 102.3846 | 17.98 | 1828.0921 | 1110.9016 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1144.9852 | 1253.6503 | 1362.3154 | 1470.9805 | 1579.6456 | 1601.6708 | 1623.6961 | 1523.5467 | 1632.2118 | 1740.8769 | 1849.542 | 1958.2071 | 2066.8722 | 2088.8974 | 1972.9832 | 1675.9619 | 1067.4364
115 | 414000 | 0.22463 | 0.20123 | -84.2302 | -66.2502 | 1930.4768 | 1213.2862 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1247.3698 | 1356.0349 | 1464.7 | 1573.3651 | 1682.0302 | 1704.0555 | 1726.0807 | 1625.9313 | 1734.5964 | 1843.2615 | 1951.9266 | 2060.5917 | 2169.2568 | 2191.282 | 2075.3678 | 1778.3465 | 1169.8211
116 | 417600 | 0.25919 | 0.20123 | -208.64 | -274.8902 | 1846.2466 | 1129.056 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1163.1396 | 1271.8048 | 1380.4699 | 1489.135 | 1597.8001 | 1619.8253 | 1641.8505 | 1541.7011 | 1650.3662 | 1759.0313 | 1867.6964 | 1976.3615 | 2085.0266 | 2107.0519 | 1991.1377 | 1694.1164 | 1085.5909
117 | 421200 | 0.25919 | 0.20123 | -208.64 | -483.5303 | 1637.6065 | 920.416 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 954.4996 | 1063.1647 | 1171.8298 | 1280.4949 | 1389.16 | 1411.1852 | 1433.2105 | 1333.0611 | 1441.7262 | 1550.3913 | 1659.0564 | 1767.7215 | 1876.3866 | 1898.4118 | 1782.4976 | 1485.4763 | 876.9508
118 | 424800 | 0.24191 | 0.20123 | -146.4351 | -629.9654 | 1428.9665 | 711.7759 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 745.8596 | 854.5247 | 963.1898 | 1071.8549 | 1180.52 | 1202.5452 | 1224.5704 | 1124.421 | 1233.0861 | 1341.7512 | 1450.4163 | 1559.0814 | 1667.7465 | 1689.7718 | 1573.8576 | 1276.8363 | 668.3108
119 | 428400 | 0.20735 | 0.20123 | -22.0252 | -651.9906 | 1282.5314 | 565.3408 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 599.4244 | 708.0895 | 816.7546 | 925.4197 | 1034.0848 | 1056.1101 | 1078.1353 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1427.4224 | 1130.4012 | 521.8757
120 | 432000 | 0.16903 | 0.20123 | 115.9142 | -536.0764 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1034.0848 | 1056.1101 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1405.3972 | 1108.3759 | 499.8504
121 | 435600 | 0.11873 | 0.20123 | 297.0213 | -239.0551 | 1376.4204 | 659.2298 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 693.3134 | 801.9785 | 910.6436 | 1019.3087 | 1127.9738 | 1149.9991 | 1172.0243 | 1071.8749 | 1180.54 | 1289.2051 | 1397.8702 | 1506.5353 | 1615.2004 | 1637.2256 | 1521.3114 | 1224.2901 | 615.7647
122 | 439200 | 0.032197 | 0.20123 | 608.5255 | 369.4704 | 1673.4417 | 956.2511 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 990.3347 | 1098.9998 | 1207.6649 | 1316.33 | 1424.9951 | 1447.0204 | 1469.0456 | 1368.8962 | 1477.5613 | 1586.2264 | 1694.8915 | 1803.5566 | 1912.2217 | 1934.2469 | 1818.3327 | 1521.3114 | 912.7859
123 | 442800 | 0.032197 | 0.20123 | 608.5255 | 977.9959 | 2281.9671 | 1564.7766 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1598.8602 | 1707.5253 | 1816.1904 | 1924.8555 | 2033.5206 | 2055.5458 | 2077.5711 | 1977.4217 | 2086.0868 | 2194.7519 | 2303.417 | 2412.0821 | 2520.7472 | 2542.7724 | 2426.8582 | 2129.8369 | 1521.3114
124 | 446400 | 0.080492 | 0.20123 | 434.6627 | 1412.6585 | 2890.4926 | 2173.302 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2207.3857 | 2316.0508 | 2424.7159 | 2533.381 | 2642.0461 | 2664.0713 | 2686.0966 | 2585.9471 | 2694.6122 | 2803.2774 | 2911.9425 | 3020.6076 | 3129.2727 | 3151.2979 | 3035.3837 | 2738.3624 | 2129.8369
125 | 450000 | 0.1308 | 0.20123 | 253.5556 | 1666.2141 | 3325.1553 | 2607.9647 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2642.0484 | 2750.7135 | 2859.3786 | 2968.0437 | 3076.7088 | 3098.734 | 3120.7592 | 3020.6098 | 3129.2749 | 3237.94 | 3346.6051 | 3455.2702 | 3563.9353 | 3585.9606 | 3470.0464 | 3173.0251 | 2564.4996
126 | 453600 | 0.21733 | 0.20123 | -57.9486 | 1608.2655 | 3578.7109 | 2861.5203 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2895.6039 | 3004.269 | 3112.9341 | 3221.5993 | 3330.2644 | 3352.2896 | 3374.3148 | 3274.1654 | 3382.8305 | 3491.4956 | 3600.1607 | 3708.8258 | 3817.4909 | 3839.5162 | 3723.602 | 3426.5807 | 2818.0552
127 | 457200 | 0.27669 | 0.20123 | -271.6549 | 1336.6106 | 3520.7623 | 2803.5717 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2837.6554 | 2946.3205 | 3054.9856 | 3163.6507 | 3272.3158 | 3294.341 | 3316.3662 | 3216.2168 | 3324.8819 | 3433.547 | 3542.2121 | 3650.8772 | 3759.5423 | 3781.5676 | 3665.6534 | 3368.6321 | 2760.1066
128 | 460800 | 0.35215 | 0.20123 | -543.3156 | 793.295 | 3249.1074 | 2531.9168 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2566.0004 | 2674.6655 | 2783.3306 | 2891.9957 | 3000.6608 | 3022.6861 | 3044.7113 | 2944.5619 | 3053.227 | 3161.8921 | 3270.5572 | 3379.2223 | 3487.8874 | 3509.9126 | 3393.9984 | 3096.9771 | 2488.4516
129 | 464400 | 0.25154 | 0.20123 | -181.1014 | 612.1936 | 2705.7918 | 1988.6012 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 2022.6848 | 2131.3499 | 2240.015 | 2348.6801 | 2457.3452 | 2479.3705 | 2501.3957 | 2401.2463 | 2509.9114 | 2618.5765 | 2727.2416 | 2835.9067 | 2944.5718 | 2966.5971 | 2850.6829 | 2553.6616 | 1945.1361
130 | 468000 | 0.22337 | 0.20123 | -79.6814 | 532.5122 | 2524.6904 | 1807.4998 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1841.5834 | 1950.2485 | 2058.9136 | 2167.5787 | 2276.2438 | 2298.2691 | 2320.2943 | 2220.1449 | 2328.81 | 2437.4751 | 2546.1402 | 2654.8053 | 2763.4704 | 2785.4957 | 2669.5814 | 2372.5602 | 1764.0347
131 | 471600 | 0.24148 | 0.20123 | -144.88 | 387.6322 | 2445.0089 | 1727.8184 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1761.902 | 1870.5671 | 1979.2322 | 2087.8973 | 2196.5624 | 2218.5876 | 2240.6129 | 2140.4635 | 2249.1286 | 2357.7937 | 2466.4588 | 2575.1239 | 2683.789 | 2705.8142 | 2589.9 | 2292.8787 | 1684.3532
132 | 475200 | 0.25154 | 0.20123 | -181.1014 | 206.5308 | 2300.129 | 1582.9384 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1617.022 | 1725.6871 | 1834.3522 | 1943.0173 | 2051.6824 | 2073.7077 | 2095.7329 | 1995.5835 | 2104.2486 | 2212.9137 | 2321.5788 | 2430.2439 | 2538.909 | 2560.9342 | 2445.02 | 2147.9987 | 1539.4732
133 | 478800 | 0.25757 | 0.20123 | -202.8343 | 3.6965 | 2119.0276 | 1401.837 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1435.9206 | 1544.5857 | 1653.2508 | 1761.9159 | 1870.581 | 1892.6063 | 1914.6315 | 1814.4821 | 1923.1472 | 2031.8123 | 2140.4774 | 2249.1425 | 2357.8076 | 2379.8328 | 2263.9186 | 1966.8973 | 1358.3718
134 | 482400 | 0.24191 | 0.20123 | -146.4353 | -142.7388 | 1916.1933 | 1199.0027 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1233.0864 | 1341.7515 | 1450.4166 | 1559.0817 | 1667.7468 | 1689.772 | 1711.7972 | 1611.6478 | 1720.3129 | 1828.978 | 1937.6431 | 2046.3082 | 2154.9733 | 2176.9986 | 2061.0844 | 1764.0631 | 1155.5376
135 | 486000 | 0.20735 | 0.20123 | -22.0252 | -164.764 | 1769.758 | 1052.5674 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1565.3619 | 1465.2125 | 1573.8776 | 1682.5427 | 1791.2078 | 1899.8729 | 2008.538 | 2030.5632 | 1914.649 | 1617.6277 | 1009.1023
136 | 489600 | 0.20735 | 0.20123 | -22.0252 | -186.7893 | 1747.7327 | 1030.5421 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1543.3367 | 1443.1873 | 1551.8524 | 1660.5175 | 1769.1826 | 1877.8477 | 1986.5128 | 2008.538 | 1892.6238 | 1595.6025 | 987.077
137 | 493200 | 0.17279 | 0.20123 | 102.3846 | -84.4046 | 1725.7075 | 1008.5169 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 1042.6005 | 1151.2656 | 1259.9307 | 1368.5959 | 1477.261 | 1499.2862 | 1521.3114 | 1421.162 | 1529.8271 | 1638.4922 | 1747.1573 | 1855.8224 | 1964.4875 | 1986.5128 | 1870.5986 | 1573.5773 | 965.0518
138 | 496800 | 0.17279 | 0.20123 | 102.3846 | 17.98 | 1828.0921 | 1110.9016 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1144.9852 | 1253.6503 | 1362.3154 | 1470.9805 | 1579.6456 | 1601.6708 | 1623.6961 | 1523.5467 | 1632.2118 | 1740.8769 | 1849.542 | 1958.2071 | 2066.8722 | 2088.8974 | 1972.9832 | 1675.9619 | 1067.4364
139 | 500400 | 0.22463 | 0.20123 | -84.2302 | -66.2502 | 1930.4768 | 1213.2862 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1247.3698 | 1356.0349 | 1464.7 | 1573.3651 | 1682.0302 | 1704.0555 | 1726.0807 | 1625.9313 | 1734.5964 | 1843.2615 | 1951.9266 | 2060.5917 | 2169.2568 | 2191.282 | 2075.3678 | 1778.3465 | 1169.8211
140 | 504000 | 0.25919 | 0.20123 | -208.64 | -274.8902 | 1846.2466 | 1129.056 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1163.1396 | 1271.8048 | 1380.4699 | 1489.135 | 1597.8001 | 1619.8253 | 1641.8505 | 1541.7011 | 1650.3662 | 1759.0313 | 1867.6964 | 1976.3615 | 2085.0266 | 2107.0519 | 1991.1377 | 1694.1164 | 1085.5909
141 | 507600 | 0.25919 | 0.20123 | -208.64 | -483.5303 | 1637.6065 | 920.416 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 954.4996 | 1063.1647 | 1171.8298 | 1280.4949 | 1389.16 | 1411.1852 | 1433.2105 | 1333.0611 | 1441.7262 | 1550.3913 | 1659.0564 | 1767.7215 | 1876.3866 | 1898.4118 | 1782.4976 | 1485.4763 | 876.9508
142 | 511200 | 0.24191 | 0.20123 | -146.4351 | -629.9654 | 1428.9665 | 711.7759 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 745.8596 | 854.5247 | 963.1898 | 1071.8549 | 1180.52 | 1202.5452 | 1224.5704 | 1124.421 | 1233.0861 | 1341.7512 | 1450.4163 | 1559.0814 | 1667.7465 | 1689.7718 | 1573.8576 | 1276.8363 | 668.3108
143 | 514800 | 0.20735 | 0.20123 | -22.0252 | -651.9906 | 1282.5314 | 565.3408 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 599.4244 | 708.0895 | 816.7546 | 925.4197 | 1034.0848 | 1056.1101 | 1078.1353 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1427.4224 | 1130.4012 | 521.8757
144 | 518400 | 0.16903 | 0.20123 | 115.9142 | -536.0764 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1034.0848 | 1056.1101 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1405.3972 | 1108.3759 | 499.8504
145 | 522000 | 0.11873 | 0.20123 | 297.0213 | -239.0551 | 1376.4204 | 659.2298 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 584.6483 | 693.3134 | 801.9785 | 910.6436 | 1019.3087 | 1127.9738 | 1149.9991 | 1172.0243 | 1071.8749 | 1180.54 | 1289.2051 | 1397.8702 | 1506.5353 | 1615.2004 | 1637.2256 | 1521.3114 | 1224.2901 | 615.7647
146 | 525600 | 0.032197 | 0.20123 | 608.5255 | 369.4704 | 1673.4417 | 956.2511 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 881.6696 | 990.3347 | 1098.9998 | 1207.6649 | 1316.33 | 1424.9951 | 1447.0204 | 1469.0456 | 1368.8962 | 1477.5613 | 1586.2264 | 1694.8915 | 1803.5566 | 1912.2217 | 1934.2469 | 1818.3327 | 1521.3114 | 912.7859
147 | 529200 | 0.032197 | 0.20123 | 608.5255 | 977.9959 | 2281.9671 | 1564.7766 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1490.1951 | 1598.8602 | 1707.5253 | 1816.1904 | 1924.8555 | 2033.5206 | 2055.5458 | 2077.5711 | 1977.4217 | 2086.0868 | 2194.7519 | 2303.417 | 2412.0821 | 2520.7472 | 2542.7724 | 2426.8582 | 2129.8369 | 1521.3114
148 | 532800 | 0.080492 | 0.20123 | 434.6627 | 1412.6585 | 2890.4926 | 2173.302 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2098.7206 | 2207.3857 | 2316.0508 | 2424.7159 | 2533.381 | 2642.0461 | 2664.0713 | 2686.0966 | 2585.9471 | 2694.6122 | 2803.2774 | 2911.9425 | 3020.6076 | 3129.2727 | 3151.2979 | 3035.3837 | 2738.3624 | 2129.8369
149 | 536400 | 0.1308 | 0.20123 | 253.5556 | 1666.2141 | 3325.1553 | 2607.9647 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2533.3832 | 2642.0484 | 2750.7135 | 2859.3786 | 2968.0437 | 3076.7088 | 3098.734 | 3120.7592 | 3020.6098 | 3129.2749 | 3237.94 | 3346.6051 | 3455.2702 | 3563.9353 | 3585.9606 | 3470.0464 | 3173.0251 | 2564.4996
150 | 540000 | 0.21733 | 0.20123 | -57.9486 | 1608.2655 | 3578.7109 | 2861.5203 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2786.9388 | 2895.6039 | 3004.269 | 3112.9341 | 3221.5993 | 3330.2644 | 3352.2896 | 3374.3148 | 3274.1654 | 3382.8305 | 3491.4956 | 3600.1607 | 3708.8258 | 3817.4909 | 3839.5162 | 3723.602 | 3426.5807 | 2818.0552
151 | 543600 | 0.27669 | 0.20123 | -271.6549 | 1336.6106 | 3520.7623 | 2803.5717 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2728.9903 | 2837.6554 | 2946.3205 | 3054.9856 | 3163.6507 | 3272.3158 | 3294.341 | 3316.3662 | 3216.2168 | 3324.8819 | 3433.547 | 3542.2121 | 3650.8772 | 3759.5423 | 3781.5676 | 3665.6534 | 3368.6321 | 2760.1066
152 | 547200 | 0.35215 | 0.20123 | -543.3156 | 793.295 | 3249.1074 | 2531.9168 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2457.3353 | 2566.0004 | 2674.6655 | 2783.3306 | 2891.9957 | 3000.6608 | 3022.6861 | 3044.7113 | 2944.5619 | 3053.227 | 3161.8921 | 3270.5572 | 3379.2223 | 3487.8874 | 3509.9126 | 3393.9984 | 3096.9771 | 2488.4516
153 | 550800 | 0.25154 | 0.20123 | -181.1014 | 612.1936 | 2705.7918 | 1988.6012 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 1914.0197 | 2022.6848 | 2131.3499 | 2240.015 | 2348.6801 | 2457.3452 | 2479.3705 | 2501.3957 | 2401.2463 | 2509.9114 | 2618.5765 | 2727.2416 | 2835.9067 | 2944.5718 | 2966.5971 | 2850.6829 | 2553.6616 | 1945.1361
154 | 554400 | 0.22337 | 0.20123 | -79.6814 | 532.5122 | 2524.6904 | 1807.4998 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1732.9183 | 1841.5834 | 1950.2485 | 2058.9136 | 2167.5787 | 2276.2438 | 2298.2691 | 2320.2943 | 2220.1449 | 2328.81 | 2437.4751 | 2546.1402 | 2654.8053 | 2763.4704 | 2785.4957 | 2669.5814 | 2372.5602 | 1764.0347
155 | 558000 | 0.24148 | 0.20123 | -144.88 | 387.6322 | 2445.0089 | 1727.8184 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1653.2369 | 1761.902 | 1870.5671 | 1979.2322 | 2087.8973 | 2196.5624 | 2218.5876 | 2240.6129 | 2140.4635 | 2249.1286 | 2357.7937 | 2466.4588 | 2575.1239 | 2683.789 | 2705.8142 | 2589.9 | 2292.8787 | 1684.3532
156 | 561600 | 0.25154 | 0.20123 | -181.1014 | 206.5308 | 2300.129 | 1582.9384 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1508.3569 | 1617.022 | 1725.6871 | 1834.3522 | 1943.0173 | 2051.6824 | 2073.7077 | 2095.7329 | 1995.5835 | 2104.2486 | 2212.9137 | 2321.5788 | 2430.2439 | 2538.909 | 2560.9342 | 2445.02 | 2147.9987 | 1539.4732
157 | 565200 | 0.25757 | 0.20123 | -202.8343 | 3.6965 | 2119.0276 | 1401.837 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1327.2555 | 1435.9206 | 1544.5857 | 1653.2508 | 1761.9159 | 1870.581 | 1892.6063 | 1914.6315 | 1814.4821 | 1923.1472 | 2031.8123 | 2140.4774 | 2249.1425 | 2357.8076 | 2379.8328 | 2263.9186 | 1966.8973 | 1358.3718
158 | 568800 | 0.24191 | 0.20123 | -146.4353 | -142.7388 | 1916.1933 | 1199.0027 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1124.4213 | 1233.0864 | 1341.7515 | 1450.4166 | 1559.0817 | 1667.7468 | 1689.772 | 1711.7972 | 1611.6478 | 1720.3129 | 1828.978 | 1937.6431 | 2046.3082 | 2154.9733 | 2176.9986 | 2061.0844 | 1764.0631 | 1155.5376
159 | 572400 | 0.20735 | 0.20123 | -22.0252 | -164.764 | 1769.758 | 1052.5674 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1565.3619 | 1465.2125 | 1573.8776 | 1682.5427 | 1791.2078 | 1899.8729 | 2008.538 | 2030.5632 | 1914.649 | 1617.6277 | 1009.1023
160 | 576000 | 0.20735 | 0.20123 | -22.0252 | -186.7893 | 1747.7327 | 1030.5421 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1543.3367 | 1443.1873 | 1551.8524 | 1660.5175 | 1769.1826 | 1877.8477 | 1986.5128 | 2008.538 | 1892.6238 | 1595.6025 | 987.077
161 | 579600 | 0.17279 | 0.20123 | 102.3846 | -84.4046 | 1725.7075 | 1008.5169 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 933.9354 | 1042.6005 | 1151.2656 | 1259.9307 | 1368.5959 | 1477.261 | 1499.2862 | 1521.3114 | 1421.162 | 1529.8271 | 1638.4922 | 1747.1573 | 1855.8224 | 1964.4875 | 1986.5128 | 1870.5986 | 1573.5773 | 965.0518
162 | 583200 | 0.17279 | 0.20123 | 102.3846 | 17.98 | 1828.0921 | 1110.9016 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1036.3201 | 1144.9852 | 1253.6503 | 1362.3154 | 1470.9805 | 1579.6456 | 1601.6708 | 1623.6961 | 1523.5467 | 1632.2118 | 1740.8769 | 1849.542 | 1958.2071 | 2066.8722 | 2088.8974 | 1972.9832 | 1675.9619 | 1067.4364
163 | 586800 | 0.22463 | 0.20123 | -84.2302 | -66.2502 | 1930.4768 | 1213.2862 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1138.7047 | 1247.3698 | 1356.0349 | 1464.7 | 1573.3651 | 1682.0302 | 1704.0555 | 1726.0807 | 1625.9313 | 1734.5964 | 1843.2615 | 1951.9266 | 2060.5917 | 2169.2568 | 2191.282 | 2075.3678 | 1778.3465 | 1169.8211
164 | 590400 | 0.25919 | 0.20123 | -208.64 | -274.8902 | 1846.2466 | 1129.056 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1054.4745 | 1163.1396 | 1271.8048 | 1380.4699 | 1489.135 | 1597.8001 | 1619.8253 | 1641.8505 | 1541.7011 | 1650.3662 | 1759.0313 | 1867.6964 | 1976.3615 | 2085.0266 | 2107.0519 | 1991.1377 | 1694.1164 | 1085.5909
165 | 594000 | 0.25919 | 0.20123 | -208.64 | -483.5303 | 1637.6065 | 920.416 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 845.8345 | 954.4996 | 1063.1647 | 1171.8298 | 1280.4949 | 1389.16 | 1411.1852 | 1433.2105 | 1333.0611 | 1441.7262 | 1550.3913 | 1659.0564 | 1767.7215 | 1876.3866 | 1898.4118 | 1782.4976 | 1485.4763 | 876.9508
166 | 597600 | 0.24191 | 0.20123 | -146.4351 | -629.9654 | 1428.9665 | 711.7759 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 637.1945 | 745.8596 | 854.5247 | 963.1898 | 1071.8549 | 1180.52 | 1202.5452 | 1224.5704 | 1124.421 | 1233.0861 | 1341.7512 | 1450.4163 | 1559.0814 | 1667.7465 | 1689.7718 | 1573.8576 | 1276.8363 | 668.3108
167 | 601200 | 0.20735 | 0.20123 | -22.0252 | -651.9906 | 1282.5314 | 565.3408 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 490.7593 | 599.4244 | 708.0895 | 816.7546 | 925.4197 | 1034.0848 | 1056.1101 | 1078.1353 | 977.9859 | 1086.651 | 1195.3161 | 1303.9812 | 1412.6463 | 1521.3114 | 1543.3367 | 1427.4224 | 1130.4012 | 521.8757
168 | 604800 | 0.16903 | 0.20123 | 115.9142 | -536.0764 | 1260.5062 | 543.3156 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 468.7341 | 577.3992 | 686.0643 | 794.7294 | 903.3945 | 1012.0596 | 1034.0848 | 1056.1101 | 955.9607 | 1064.6258 | 1173.2909 | 1281.956 | 1390.6211 | 1499.2862 | 1521.3114 | 1405.3972 | 1108.3759 | 499.8504

## Sheet2
| Power_Out_Start | Tank_Emerg_Vol | Pumped_Flow | In_-_Out | Cumulative_Sum
0 | 0 | 4931.2365 | 0.20123 | 115.9142 | 115.9142
1 | 1 | 5764.3356 | 0.20123 | 297.0213 | 412.9355 | 4252.1513
2 | 2 | 6170.022 | 0.20123 | 608.5255 | 1021.461
3 | 3 | 6887.2126 | 0.20123 | 608.5255 | 1629.9865 | 1933.9473
4 | 4 | 7517.7633 | 0.20123 | 434.6627 | 2064.6491
5 | 5 | 7974.4512 | 0.20123 | 253.5556 | 2318.2047
6 | 6 | 8127.8574 | 0.20123 | -57.9486 | 2260.2562
7 | 7 | 8236.5225 | 0.20123 | -271.6549 | 1988.6012
8 | 8 | 8345.1876 | 0.20123 | -543.3156 | 1445.2856
9 | 9 | 8453.8527 | 0.20123 | -181.1014 | 1264.1842
10 | 10 | 8562.5178 | 0.20123 | -79.6814 | 1184.5028
11 | 11 | 8671.1829 | 0.20123 | -144.88 | 1039.6228
12 | 12 | 8693.2081 | 0.20123 | -181.1014 | 858.5214
13 | 13 | 8577.2939 | 0.20123 | -202.8343 | 655.6871
14 | 14 | 8280.2726 | 0.20123 | -146.4353 | 509.2518
15 | 15 | 7671.7472 | 0.20123 | -22.0252 | 487.2266
16 | 16 | 7063.2217 | 0.20123 | -22.0252 | 465.2013
17 | 17 | 7097.3053 | 0.20123 | 102.3846 | 567.586
18 | 18 | 7205.9704 | 0 | -622.0494 | -54.4634
19 | 19 | 7314.6355 | 0 | -808.6642 | -863.1276
20 | 20 | 7423.3006 | 0 | -933.0741 | -1796.2016
21 | 21 | 7531.9657 | 0.23142 | -99.9749 | -1896.1766
22 | 22 | 7640.6308 | 0.23142 | -37.77 | -1933.9466
23 | 23 | 7749.2959 | 0.23142 | 86.6399 | -1847.3067
24 | 24 | 7857.961 | 0.23142 | 224.5793 | -1622.7274
25 | 90000 | 0.11873 | 0.23142 | 405.6864 | -1217.041
26 | 93600 | 0.032197 | 0.23142 | 717.1906 | -499.8504
27 | 97200 | 0.032197 | 0.23142 | 717.1906 | 217.3401
28 | 100800 | 0.080492 | 0.23142 | 543.3278 | 760.6679
29 | 104400 | 0.1308 | 0.23142 | 362.2207 | 1122.8886
30 | 108000 | 0.21733 | 0.23142 | 50.7165 | 1173.6051
31 | 111600 | 0.27669 | 0.23142 | -162.9898 | 1010.6153
32 | 115200 | 0.35215 | 0.23142 | -434.6505 | 575.9648
33 | 118800 | 0.25154 | 0.23142 | -72.4363 | 503.5285
34 | 122400 | 0.22337 | 0.23142 | 28.9837 | 532.5122
35 | 126000 | 0.24148 | 0.23142 | -36.2149 | 496.2973
36 | 129600 | 0.25154 | 0.23142 | -72.4363 | 423.861
37 | 133200 | 0.25757 | 0.23142 | -94.1692 | 329.6918
38 | 136800 | 0.24191 | 0.23142 | -37.7702 | 291.9216
39 | 140400 | 0.20735 | 0.23142 | 86.6399 | 378.5615
40 | 144000 | 0.20735 | 0.23142 | 86.6399 | 465.2013
41 | 147600 | 0.17279 | 0.23142 | 211.0497 | 676.2511
42 | 151200 | 0.17279 | 0.20123 | 102.3846 | 778.6357
43 | 154800 | 0.22463 | 0.20123 | -84.2302 | 694.4055
44 | 158400 | 0.25919 | 0.20123 | -208.64 | 485.7655
45 | 162000 | 0.25919 | 0.20123 | -208.64 | 277.1254
46 | 165600 | 0.24191 | 0.20123 | -146.4351 | 130.6903
47 | 169200 | 0.20735 | 0.20123 | -22.0252 | 108.6651
48 | 172800 | 0.16903 | 0.20123 | 115.9142 | 224.5793
49 | 176400 | 0.11873 | 0.20123 | 297.0213 | 521.6006
50 | 180000 | 0.032197 | 0.20123 | 608.5255 | 1130.1261
51 | 183600 | 0.032197 | 0.20123 | 608.5255 | 1738.6516
52 | 187200 | 0.080492 | 0.20123 | 434.6627 | 2173.3142
53 | 190800 | 0.1308 | 0.20123 | 253.5556 | 2426.8698
54 | 194400 | 0.21733 | 0.20123 | -57.9486 | 2368.9213
55 | 198000 | 0.27669 | 0.20123 | -271.6549 | 2097.2663
56 | 201600 | 0.35215 | 0.20123 | -543.3156 | 1553.9507
57 | 205200 | 0.25154 | 0.20123 | -181.1014 | 1372.8493
58 | 208800 | 0.22337 | 0.20123 | -79.6814 | 1293.1679
59 | 212400 | 0.24148 | 0.20123 | -144.88 | 1148.2879
60 | 216000 | 0.25154 | 0.20123 | -181.1014 | 967.1865
61 | 219600 | 0.25757 | 0.20123 | -202.8343 | 764.3523
62 | 223200 | 0.24191 | 0.20123 | -146.4353 | 617.9169
63 | 226800 | 0.20735 | 0.20123 | -22.0252 | 595.8917
64 | 230400 | 0.20735 | 0.20123 | -22.0252 | 573.8664
65 | 234000 | 0.17279 | 0.20123 | 102.3846 | 676.2511
66 | 237600 | 0.17279 | 0.20123 | 102.3846 | 778.6357
67 | 241200 | 0.22463 | 0.20123 | -84.2302 | 694.4055
68 | 244800 | 0.25919 | 0.20123 | -208.64 | 485.7655
69 | 248400 | 0.25919 | 0.20123 | -208.64 | 277.1254
70 | 252000 | 0.24191 | 0.20123 | -146.4351 | 130.6903
71 | 255600 | 0.20735 | 0.20123 | -22.0252 | 108.6651
72 | 259200 | 0.16903 | 0.20123 | 115.9142 | 224.5793
73 | 262800 | 0.11873 | 0.20123 | 297.0213 | 521.6006
74 | 266400 | 0.032197 | 0.20123 | 608.5255 | 1130.1261
75 | 270000 | 0.032197 | 0.20123 | 608.5255 | 1738.6516
76 | 273600 | 0.080492 | 0.20123 | 434.6627 | 2173.3142
77 | 277200 | 0.1308 | 0.20123 | 253.5556 | 2426.8698
78 | 280800 | 0.21733 | 0.20123 | -57.9486 | 2368.9213
79 | 284400 | 0.27669 | 0.20123 | -271.6549 | 2097.2663
80 | 288000 | 0.35215 | 0.20123 | -543.3156 | 1553.9507
81 | 291600 | 0.25154 | 0.20123 | -181.1014 | 1372.8493
82 | 295200 | 0.22337 | 0.20123 | -79.6814 | 1293.1679
83 | 298800 | 0.24148 | 0.20123 | -144.88 | 1148.2879
84 | 302400 | 0.25154 | 0.20123 | -181.1014 | 967.1865
85 | 306000 | 0.25757 | 0.20123 | -202.8343 | 764.3523
86 | 309600 | 0.24191 | 0.20123 | -146.4353 | 617.9169
87 | 313200 | 0.20735 | 0.20123 | -22.0252 | 595.8917
88 | 316800 | 0.20735 | 0.20123 | -22.0252 | 573.8664
89 | 320400 | 0.17279 | 0.20123 | 102.3846 | 676.2511
90 | 324000 | 0.17279 | 0.20123 | 102.3846 | 778.6357
91 | 327600 | 0.22463 | 0.20123 | -84.2302 | 694.4055
92 | 331200 | 0.25919 | 0.20123 | -208.64 | 485.7655
93 | 334800 | 0.25919 | 0.20123 | -208.64 | 277.1254
94 | 338400 | 0.24191 | 0.20123 | -146.4351 | 130.6903
95 | 342000 | 0.20735 | 0.20123 | -22.0252 | 108.6651
96 | 345600 | 0.16903 | 0.20123 | 115.9142 | 224.5793
97 | 349200 | 0.11873 | 0.20123 | 297.0213 | 521.6006
98 | 352800 | 0.032197 | 0.20123 | 608.5255 | 1130.1261
99 | 356400 | 0.032197 | 0.20123 | 608.5255 | 1738.6516
100 | 360000 | 0.080492 | 0.20123 | 434.6627 | 2173.3142
101 | 363600 | 0.1308 | 0.20123 | 253.5556 | 2426.8698
102 | 367200 | 0.21733 | 0.20123 | -57.9486 | 2368.9213
103 | 370800 | 0.27669 | 0.20123 | -271.6549 | 2097.2663
104 | 374400 | 0.35215 | 0.20123 | -543.3156 | 1553.9507
105 | 378000 | 0.25154 | 0.20123 | -181.1014 | 1372.8493
106 | 381600 | 0.22337 | 0.20123 | -79.6814 | 1293.1679
107 | 385200 | 0.24148 | 0.20123 | -144.88 | 1148.2879
108 | 388800 | 0.25154 | 0.20123 | -181.1014 | 967.1865
109 | 392400 | 0.25757 | 0.20123 | -202.8343 | 764.3523
110 | 396000 | 0.24191 | 0.20123 | -146.4353 | 617.9169
111 | 399600 | 0.20735 | 0.20123 | -22.0252 | 595.8917
112 | 403200 | 0.20735 | 0.20123 | -22.0252 | 573.8664
113 | 406800 | 0.17279 | 0.20123 | 102.3846 | 676.2511
114 | 410400 | 0.17279 | 0.20123 | 102.3846 | 778.6357
115 | 414000 | 0.22463 | 0.20123 | -84.2302 | 694.4055
116 | 417600 | 0.25919 | 0.20123 | -208.64 | 485.7655
117 | 421200 | 0.25919 | 0.20123 | -208.64 | 277.1254
118 | 424800 | 0.24191 | 0.20123 | -146.4351 | 130.6903
119 | 428400 | 0.20735 | 0.20123 | -22.0252 | 108.6651
120 | 432000 | 0.16903 | 0.20123 | 115.9142 | 224.5793
121 | 435600 | 0.11873 | 0.20123 | 297.0213 | 521.6006
122 | 439200 | 0.032197 | 0.20123 | 608.5255 | 1130.1261
123 | 442800 | 0.032197 | 0.20123 | 608.5255 | 1738.6516
124 | 446400 | 0.080492 | 0.20123 | 434.6627 | 2173.3142
125 | 450000 | 0.1308 | 0.20123 | 253.5556 | 2426.8698
126 | 453600 | 0.21733 | 0.20123 | -57.9486 | 2368.9213
127 | 457200 | 0.27669 | 0.20123 | -271.6549 | 2097.2663
128 | 460800 | 0.35215 | 0.20123 | -543.3156 | 1553.9507
129 | 464400 | 0.25154 | 0.20123 | -181.1014 | 1372.8493
130 | 468000 | 0.22337 | 0.20123 | -79.6814 | 1293.1679
131 | 471600 | 0.24148 | 0.20123 | -144.88 | 1148.2879
132 | 475200 | 0.25154 | 0.20123 | -181.1014 | 967.1865
133 | 478800 | 0.25757 | 0.20123 | -202.8343 | 764.3523
134 | 482400 | 0.24191 | 0.20123 | -146.4353 | 617.9169
135 | 486000 | 0.20735 | 0.20123 | -22.0252 | 595.8917
136 | 489600 | 0.20735 | 0.20123 | -22.0252 | 573.8664
137 | 493200 | 0.17279 | 0.20123 | 102.3846 | 676.2511
138 | 496800 | 0.17279 | 0.20123 | 102.3846 | 778.6357
139 | 500400 | 0.22463 | 0.20123 | -84.2302 | 694.4055
140 | 504000 | 0.25919 | 0.20123 | -208.64 | 485.7655
141 | 507600 | 0.25919 | 0.20123 | -208.64 | 277.1254
142 | 511200 | 0.24191 | 0.20123 | -146.4351 | 130.6903
143 | 514800 | 0.20735 | 0.20123 | -22.0252 | 108.6651
144 | 518400 | 0.16903 | 0.20123 | 115.9142 | 224.5793
145 | 522000 | 0.11873 | 0.20123 | 297.0213 | 521.6006
146 | 525600 | 0.032197 | 0.20123 | 608.5255 | 1130.1261
147 | 529200 | 0.032197 | 0.20123 | 608.5255 | 1738.6516
148 | 532800 | 0.080492 | 0.20123 | 434.6627 | 2173.3142
149 | 536400 | 0.1308 | 0.20123 | 253.5556 | 2426.8698
150 | 540000 | 0.21733 | 0.20123 | -57.9486 | 2368.9213
151 | 543600 | 0.27669 | 0.20123 | -271.6549 | 2097.2663
152 | 547200 | 0.35215 | 0.20123 | -543.3156 | 1553.9507
153 | 550800 | 0.25154 | 0.20123 | -181.1014 | 1372.8493
154 | 554400 | 0.22337 | 0.20123 | -79.6814 | 1293.1679
155 | 558000 | 0.24148 | 0.20123 | -144.88 | 1148.2879
156 | 561600 | 0.25154 | 0.20123 | -181.1014 | 967.1865
157 | 565200 | 0.25757 | 0.20123 | -202.8343 | 764.3523
158 | 568800 | 0.24191 | 0.20123 | -146.4353 | 617.9169
159 | 572400 | 0.20735 | 0.20123 | -22.0252 | 595.8917
160 | 576000 | 0.20735 | 0.20123 | -22.0252 | 573.8664
161 | 579600 | 0.17279 | 0.20123 | 102.3846 | 676.2511
162 | 583200 | 0.17279 | 0.20123 | 102.3846 | 778.6357
163 | 586800 | 0.22463 | 0.20123 | -84.2302 | 694.4055
164 | 590400 | 0.25919 | 0.20123 | -208.64 | 485.7655
165 | 594000 | 0.25919 | 0.20123 | -208.64 | 277.1254
166 | 597600 | 0.24191 | 0.20123 | -146.4351 | 130.6903
167 | 601200 | 0.20735 | 0.20123 | -22.0252 | 108.6651
168 | 604800 | 0.16903 | 0.20123 | 115.9142 | 224.5793
166 | 597600 | 0.24191 | 0.20104 | 0
167 | 601200 | 0.20735 | 0.20104 | 0
168 | 604800 | 0.16903 | 0.20104 | 0