## Summary
Summary of results for tank connected to each node
Column1 | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
1 | pump2 | 0 | 31.55 | 0.44 | 0.44 | 1.83 | 4.35 | 118.13 | 58.13 | 5.08 | 20.1 | 22 | J38 | [] | 11574.05 | 301648.66 | 0 | 313222.71 | 2644.67 | 27308.18 | 30619.58
0 | J38 | 7.98 | 31.55 | 0.44 | 0.44 | 1.83 | 4.35 | 118.1 | 18.1 | 5.08 | 20.1 | 22 | J38 | [] | 11574.05 | 301038.26 | 0 | 312612.31 | 2639.79 | 27254.97 | 30561.62
[22 empty] | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc)
[22 empty] | J38 | 7.98 | 31.55 | 0.44 | 0.44 | 1.83 | 4.35 | 118.1 | 18.1 | 5.08 | 20.1
[22 empty] | pump2 | 0 | 31.55 | 0.44 | 0.44 | 1.83 | 4.35 | 118.13 | 58.13 | 5.08 | 20.1
[22 empty] | Node | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
[22 empty] | J38 | 22 | J38 | [] | 11574.05 | 301038.26 | 0 | 312612.31 | 2639.79 | 27254.97 | 30561.62
[22 empty] | pump2 | 22 | J38 | [] | 11574.05 | 301648.66 | 0 | 313222.71 | 2644.67 | 27308.18 | 30619.58

## J38
This sheet contains the results for tank connected to node: J38
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 31.55 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 0.44 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 0.44 | L/s |  | Critical Node | J38
Cost: | € 1.83 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4.35 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 118.1 | m above sea level |  | Pump Cost | € 11,574.05
Tank height above ground | 18.1 | m above nearest node |  | Tank Cost | € 301,038.26
Tank volume | 5.08 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 312,612.31
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost

## pump2
This sheet contains the results for tank connected to node: pump2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 31.55 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 0.44 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 0.44 | L/s |  | Critical Node | J38
Cost: | € 1.83 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4.35 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 118.13 | m above sea level |  | Pump Cost | € 11,574.05
Tank height above ground | 58.13 | m above nearest node |  | Tank Cost | € 301,648.66
Tank volume | 5.08 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 313,222.71
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost