## Summary
Summary of results for tank connected to each node
Column1 | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
0 | a01 | 0 | 46.56 | 102.81 | 102.79 | € 631.17 | 1502.79 | 42.62 | 42.62 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 708327.68 | 163045 | 1778878.01 | 28032.69 | 155090.69 | 413501.65
1 | a02 | 0.48 | 44.57 | 102.81 | 102.78 | € 604.15 | 1438.46 | 39.57 | 39.57 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 694877.43 | 163045 | 1765427.77 | 27925.09 | 153918.04 | 402359.16
3 | a04 | 0.76 | 43.57 | 102.81 | 102.78 | € 590.50 | 1405.96 | 38.02 | 38.02 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 688065.9 | 163045 | 1758616.23 | 27870.6 | 153324.18 | 396728.17
5 | a06 | 0.9 | 43.1 | 102.81 | 102.78 | € 584.22 | 1391 | 37.31 | 37.31 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 684940.42 | 163045 | 1755490.76 | 27845.6 | 153051.68 | 394137.66
6 | a07 | 1 | 42.8 | 102.81 | 102.78 | € 580.16 | 1381.33 | 36.85 | 36.85 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 682913.74 | 163045 | 1753464.07 | 27829.38 | 152874.99 | 392462.84
7 | a08 | 1.19 | 43.04 | 102.81 | 102.73 | € 583.36 | 1388.96 | 37.04 | 37.04 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 683745.3 | 287760 | 1879010.63 | 28459.61 | 163820.71 | 405207.79
4 | a05 | 1.24 | 43.58 | 102.81 | 102.74 | € 590.71 | 1406.45 | 38.09 | 38.09 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 688371.03 | 267646 | 1863522.37 | 28396.04 | 162470.37 | 406475.09
2 | a03 | 1.32 | 44.08 | 102.81 | 102.74 | € 597.52 | 1422.67 | 38.96 | 38.96 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 692198.85 | 290916 | 1890620.19 | 28543.02 | 164832.88 | 411470.65
9 | a10 | 1.32 | 43.19 | 102.81 | 102.78 | € 585.13 | 1393.17 | 37.11 | 37.11 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 684038.01 | 329133 | 1920676.34 | 28668.82 | 167453.32 | 409695.75
13 | a14 | 1.34 | 41.98 | 102.81 | 102.81 | € 569.03 | 1354.83 | 35.6 | 35.6 | 1469.6 | 20.03 | 6 | e05 | [] | 907505.33 | 677395.58 | 163045 | 1747945.91 | 27785.24 | 152393.89 | 387875.1
15 | a16 | 1.49 | 41.79 | 102.81 | 102.78 | € 566.42 | 1348.61 | 35.28 | 35.28 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 675983.7 | 163045 | 1746534.04 | 27773.94 | 152270.8 | 386786.27
16 | a17 | 1.67 | 41.04 | 102.81 | 102.75 | € 556.17 | 1324.22 | 34.46 | 34.46 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 672388.26 | 245969 | 1825862.59 | 28159.8 | 159187.02 | 390349.57
18 | a19 | 1.67 | 39.79 | 102.81 | 102.81 | € 538.88 | 1283.05 | 32.74 | 32.74 | 1469.6 | 20.1 | 16 | e05 | [] | 907505.33 | 664798.11 | 233089 | 1805392.44 | 28034.68 | 157402.34 | 382128.16
14 | a15 | 1.8 | 42.75 | 102.81 | 102.73 | € 579.32 | 1379.34 | 36.49 | 36.49 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 681327.98 | 331633 | 1920466.31 | 28659.64 | 167435 | 407547.45
21 | b01 | 1.92 | 37.66 | 102.81 | 102.77 | € 510.07 | 1214.45 | 30.11 | 30.11 | 1469.6 | 20.09 | 16 | e05 | [] | 907505.33 | 653204.09 | 322369 | 1883078.43 | 28388.32 | 164175.36 | 378738.68
17 | a18 | 2.12 | 41.57 | 102.81 | 102.81 | € 563.10 | 1340.71 | 34.88 | 34.88 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 674207.34 | 298850 | 1880562.67 | 28438.76 | 163956.02 | 397925.21
8 | a09 | 2.22 | 43.07 | 102.81 | 102.78 | € 583.51 | 1389.3 | 36.96 | 36.96 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 683393.46 | 336449 | 1927347.8 | 28700.24 | 168034.96 | 409714.79
11 | a12 | 2.23 | 43.88 | 102.81 | 102.74 | € 594.44 | 1415.34 | 37.81 | 37.81 | 1469.6 | 20.09 | 6 | e05 | [] | 907505.33 | 687130.08 | 410725 | 2005360.41 | 29101.51 | 174836.46 | 420909.18
19 | a20 | 2.29 | 40.59 | 102.81 | 102.78 | € 549.76 | 1308.96 | 33.65 | 33.65 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 668814.71 | 303896 | 1880216.05 | 28420.84 | 163925.8 | 393009.99
22 | b02 | 2.3 | 38.11 | 102.81 | 102.81 | € 515.89 | 1228.31 | 30.25 | 30.25 | 1469.6 | 20.07 | 16 | e05 | [] | 907505.33 | 653806.02 | 393809 | 1955120.35 | 28601.82 | 170456.3 | 387358.8
33 | c01 | 2.38 | 34.77 | 102.81 | 102.78 | € 470.44 | 1120.1 | 26.58 | 26.58 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 637606.68 | 502778 | 2047890.01 | 28729.39 | 178544.38 | 378985.77
10 | a11 | 2.46 | 43.27 | 102.81 | 102.76 | € 586.20 | 1395.71 | 37.16 | 37.16 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 684250.3 | 363666 | 1955421.64 | 28843.18 | 170482.57 | 413287.93
48 | e01 | 2.53 | 34.88 | 102.81 | 102.78 | € 471.90 | 1123.57 | 26.59 | 26.59 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 637652.08 | 546906 | 2092063.41 | 28849.59 | 182395.62 | 383487.91
34 | c02 | 2.56 | 35.57 | 102.81 | 102.81 | € 480.85 | 1144.88 | 26.77 | 26.77 | 1469.6 | 20.02 | 16 | b08 | [] | 907505.33 | 638459.81 | 531020 | 2076985.14 | 28877.43 | 181081.03 | 385469.08
23 | b03 | 2.57 | 38.39 | 102.81 | 102.74 | € 519.47 | 1236.83 | 30.41 | 30.41 | 1469.6 | 20.09 | 16 | e05 | [] | 907505.33 | 654512.62 | 441685 | 2003702.96 | 28748.89 | 174691.95 | 393046.56
37 | c05 | 2.77 | 35.94 | 102.81 | 102.73 | € 485.50 | 1155.96 | 26.92 | 26.92 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 639117.45 | 577724 | 2124346.79 | 29015.41 | 185210.23 | 391434.16
49 | e02 | 2.77 | 36.79 | 102.81 | 102.81 | € 496.74 | 1182.71 | 26.76 | 26.76 | 1469.6 | 19.94 | 16 | b08 | [] | 907505.33 | 638413 | 508877 | 2054795.33 | 28665.54 | 179146.42 | 389120.82
20 | a21 | 2.79 | 40.96 | 102.81 | 102.76 | € 554.80 | 1320.96 | 34.03 | 34.03 | 1469.6 | 20.1 | 6 | e05 | [] | 907505.33 | 670472.17 | 366737 | 1944714.5 | 28748.31 | 169549.07 | 400800.57
35 | c03 | 2.81 | 35.86 | 102.81 | 102.76 | € 484.61 | 1153.84 | 27.05 | 27.05 | 1469.6 | 20.09 | 16 | b08 | [] | 907505.33 | 639708.34 | 591995 | 2139208.67 | 29173.93 | 186505.96 | 392563.33
40 | d01 | 2.89 | 35.54 | 102.81 | 102.77 | € 480.44 | 1143.91 | 27.21 | 27.21 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 640393.26 | 598510 | 2146408.6 | 29230.34 | 187133.68 | 391724.73
36 | c04 | 3.01 | 36 | 102.81 | 102.75 | € 486.38 | 1158.06 | 27.18 | 27.18 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 640275.96 | 628400 | 2176181.3 | 29360.49 | 189729.4 | 396620.04
24 | b04 | 3.02 | 38.86 | 102.81 | 102.81 | € 525.60 | 1251.42 | 30.73 | 30.73 | 1469.6 | 20 | 16 | e05 | [] | 907505.33 | 655917.94 | 499942 | 2063365.27 | 29051.42 | 179893.59 | 400787.33
50 | e03 | 3.05 | 37.34 | 102.81 | 102.74 | € 503.84 | 1199.61 | 27.27 | 27.27 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 640658.65 | 571627 | 2119790.98 | 28997.25 | 184813.04 | 397710.96
56 | f01 | 3.14 | 36.78 | 102.81 | 102.78 | € 496.40 | 1181.9 | 27.45 | 27.45 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 641445.31 | 649697 | 2198647.65 | 29393.89 | 191688.12 | 402268.03
26 | b06 | 3.21 | 39.12 | 102.81 | 102.77 | € 528.91 | 1259.32 | 31 | 31 | 1469.6 | 20.1 | 16 | e05 | [] | 907505.33 | 657107.38 | 525241 | 2089853.71 | 29122.83 | 182202.97 | 404379.68
39 | c07 | 3.23 | 37.74 | 102.81 | 102.74 | € 509.25 | 1212.49 | 27.82 | 27.82 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 643113.37 | 580826 | 2131444.71 | 29145.32 | 185829.06 | 400849.86
29 | b09 | 3.24 | 39.05 | 102.81 | 102.77 | € 528.07 | 1257.3 | 30.97 | 30.97 | 1469.6 | 20.1 | 16 | e05 | [] | 907505.33 | 656964.98 | 514126 | 2078596.31 | 29081.59 | 181221.5 | 403047.21
42 | d03 | 3.26 | 36.61 | 102.81 | 102.82 | € 494.42 | 1177.2 | 27.6 | 27.6 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 642140.34 | 581206 | 2130851.67 | 29157.8 | 185777.36 | 395400
27 | b07 | 3.36 | 39.22 | 102.81 | 102.75 | € 530.30 | 1262.63 | 31.1 | 31.1 | 1469.6 | 20.1 | 16 | e05 | [] | 907505.33 | 657557.02 | 567187 | 2132249.35 | 29290.26 | 185899.21 | 408750.15
51 | e04 | 3.38 | 37.82 | 102.81 | 102.81 | € 510.17 | 1214.7 | 27.59 | 27.59 | 1469.6 | 19.97 | 6 | b12 | [] | 907505.33 | 642088.19 | 637809 | 2187402.52 | 29292.51 | 190707.72 | 406213.46
44 | d05 | 3.44 | 36.85 | 102.81 | 102.8 | € 497.63 | 1184.82 | 27.87 | 27.87 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 643305.95 | 648524 | 2199335.28 | 29503.71 | 191748.07 | 402885.05
25 | b05 | 3.45 | 39.29 | 102.81 | 102.74 | € 531.13 | 1264.59 | 31.14 | 31.14 | 1469.6 | 20.1 | 16 | e05 | [] | 907505.33 | 657716 | 570414 | 2135635.33 | 29372.26 | 186194.42 | 409428.01
53 | e06 | 3.51 | 36.69 | 102.81 | 102.77 | € 495.27 | 1179.22 | 27.49 | 27.49 | 1469.6 | 20.1 | 16 | b08 | [] | 907505.33 | 641657.77 | 661233 | 2210396.1 | 29453.27 | 192712.4 | 402939.74
30 | b10 | 3.52 | 39.24 | 102.81 | 102.76 | € 530.54 | 1263.18 | 31.16 | 31.16 | 1469.6 | 20.1 | 16 | e05 | [] | 907505.33 | 657811.21 | 535406 | 2100722.54 | 29175.72 | 183150.56 | 405971.97
45 | d06 | 3.58 | 37.02 | 102.81 | 102.79 | € 499.79 | 1189.99 | 28.04 | 28.04 | 1469.6 | 20.1 | 6 | b12 | [] | 907505.33 | 644062.48 | 665521 | 2217088.81 | 29594.75 | 193295.91 | 405315.6
41 | d02 | 3.59 | 37.5 | 102.81 | 102.84 | € 506.28 | 1205.44 | 27.72 | 27.72 | 1469.6 | 20.08 | 16 | b08 | [] | 907505.33 | 642636.81 | 557346 | 2107488.14 | 29042.47 | 183740.42 | 397576.46
12 | a13 | 3.61 | 44.09 | 102.81 | 102.81 | € 597.06 | 1421.57 | 37.93 | 37.93 | 1469.6 | 20.01 | 6 | e05 | [] | 907505.33 | 687645.58 | 438930 | 2034080.91 | 29246.66 | 177340.44 | 424514.51
54 | e07 | 3.71 | 38.64 | 102.81 | 102.84 | € 521.11 | 1240.74 | 28.36 | 28.36 | 1469.6 | 20.08 | 6 | b12 | [] | 907505.33 | 645469.93 | 676945 | 2229920.26 | 29515.24 | 194414.61 | 414134.81
52 | e05 | 3.79 | 38.63 | 102.81 | 102.74 | € 520.81 | 1240.03 | 28.48 | 28.48 | 1469.6 | 20.1 | 6 | b12 | [] | 907505.33 | 645989.74 | 685878 | 2239373.08 | 29564.06 | 195238.75 | 414899.57
28 | b08 | 3.94 | 40.32 | 102.81 | 102.83 | € 544.79 | 1297.12 | 31.98 | 31.98 | 1469.6 | 20.09 | 6 | e05 | ['p38'] | 907505.33 | 661434.48 | 612291 | 2181230.82 | 29546.8 | 190169.64 | 418565.5
32 | b12 | 4.01 | 42.29 | 102.81 | 102.84 | € 570.82 | 1359.08 | 32.87 | 32.87 | 1469.6 | 20.08 | 6 | e05 | ['p37'] | 907505.33 | 665347.51 | 594380 | 2167232.84 | 29484.98 | 188949.24 | 426781.83
47 | d08 | 4.01 | 37.86 | 102.81 | 102.78 | € 510.87 | 1216.36 | 28.88 | 28.88 | 1469.6 | 20.09 | 6 | b12 | [] | 907505.33 | 647770.04 | 702496 | 2257771.38 | 29809.29 | 196842.8 | 413119.79
55 | e08 | 4.08 | 39.06 | 102.81 | 102.76 | € 526.51 | 1253.59 | 28.8 | 28.8 | 1469.6 | 20.09 | 6 | b12 | [] | 907505.33 | 647400.55 | 706295 | 2261200.88 | 29677.44 | 197141.8 | 418994.01
43 | d04 | 4.17 | 38.21 | 102.81 | 102.74 | € 515.51 | 1227.4 | 28.45 | 28.45 | 1469.6 | 20.09 | 6 | b12 | [] | 907505.33 | 645850.51 | 685617 | 2238972.85 | 29709.54 | 195203.86 | 413074.46
31 | b11 | 4.26 | 39.67 | 102.81 | 102.81 | € 536.21 | 1276.69 | 31.44 | 31.44 | 1469.6 | 19.98 | 6 | e05 | [] | 907505.33 | 659054.9 | 650185 | 2216745.23 | 29713.66 | 193265.95 | 418695.91
46 | d07 | 4.89 | 40.08 | 102.81 | 102.85 | € 540.43 | 1286.73 | 30.1 | 30.1 | 1469.6 | 20.06 | 6 | b12 | [] | 907505.33 | 653134.2 | 666417 | 2227056.53 | 29671.81 | 194164.94 | 421092.11
38 | c06 | 5.15 | 37.02 | 102.81 | 102.81 | € 499.79 | 1189.99 | 27 | 27 | 1469.6 | 20 | 16 | b08 | [] | 907505.33 | 639476.87 | 569284 | 2116266.2 | 28957.72 | 184505.73 | 395888.52
30 year life
[5 empty] | c01 | Min | 1120.1 | 12265095 | 5151339.9
[5 empty] | a01 | Max | 1502.79 | 16455550.5 | 6911331.21 | [9 empty] | 34515.88
1035476.4
1759991.31

## a01
This sheet contains the results for tank connected to node: a01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.56 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | e05
Cost: | € 631.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1502.79 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 42.62 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 42.62 | m above nearest node |  | Tank Cost | € 708,327.68
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,778,878.01
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a02
This sheet contains the results for tank connected to node: a02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.57 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 604.15 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1438.46 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 39.57 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 39.57 | m above nearest node |  | Tank Cost | € 694,877.43
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,765,427.77
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a03
This sheet contains the results for tank connected to node: a03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.08 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | € 597.52 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1422.67 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.96 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 38.96 | m above nearest node |  | Tank Cost | € 692,198.85
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 290,916.00
|  |  |  | Total Investment Cost | € 1,890,620.19
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 315 | 190 | 72200
p05 | 80 | 325 | 250 | 120 | 39000
p07 | 80 | 249 | 250 | 120 | 29880
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a04
This sheet contains the results for tank connected to node: a04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.57 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 590.50 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1405.96 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.02 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 38.02 | m above nearest node |  | Tank Cost | € 688,065.90
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,758,616.23
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a05
This sheet contains the results for tank connected to node: a05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.58 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | € 590.71 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1406.45 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.09 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 38.09 | m above nearest node |  | Tank Cost | € 688,371.03
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 267,646.00
|  |  |  | Total Investment Cost | € 1,863,522.37
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 225 | 100 | 38000
p05 | 80 | 325 | 225 | 100 | 32500
p07 | 80 | 249 | 315 | 190 | 47310
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a06
This sheet contains the results for tank connected to node: a06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.1 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 584.22 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1391 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.31 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 37.31 | m above nearest node |  | Tank Cost | € 684,940.42
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,755,490.76
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a07
This sheet contains the results for tank connected to node: a07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.8 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 580.16 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1381.33 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.85 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 36.85 | m above nearest node |  | Tank Cost | € 682,913.74
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,753,464.07
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980 |  | 7980
p07 | 80 | 249 | 90 | 21 | 5229 |  | 5229
p09 | 100 | 256 | 140 | 41 | 10496 |  | 10496
p11 | 80 | 111 | 110 | 28 | 3108 |  | 3108
p19 | 100 | 459 | 110 | 28 | 12852 |  | 12852
p21 | 100 | 168 | 125 | 34 | 5712 |  | 5712
p22 | 80 | 291 | 90 | 21 | 6111 |  | 6111
p33 | 80 | 106 | 110 | 28 | 2968 |  | 2968
p34 | 50 | 290 | 63 | 14 | 4060 |  | 4060
p36 | 50 | 269 | 75 | 17 | 4573 |  | 4573
p37 | 50 | 333 | 63 | 14 | 4662 |  | 4662
p38 | 80 | 380 | 110 | 28 | 10640 |  | 10640
p54 | 80 | 177 | 90 | 21 | 3717 |  | 3717
p59 | 150 | 361 | 200 | 79 | 28519 |  | 28519
p68 | 150 | 366 | 200 | 79 | 28914 |  | 28914
p69 | 150 | 452 | 160 | 52 | 23504 |  | 23504

## a08
This sheet contains the results for tank connected to node: a08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.04 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | e05
Cost: | € 583.36 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1388.96 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.04 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 37.04 | m above nearest node |  | Tank Cost | € 683,745.30
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 287,760.00
|  |  |  | Total Investment Cost | € 1,879,010.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 315 | 190 | 48640
p10 | 100 | 200 | 200 | 79 | 15800
p11 | 80 | 111 | 90 | 21 | 2331
p12 | 80 | 106 | 110 | 28 | 2968
p16 | 25 | 168 | 63 | 14 | 2352
p18 | 100 | 420 | 200 | 79 | 33180
p19 | 100 | 459 | 225 | 100 | 45900
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a09
This sheet contains the results for tank connected to node: a09
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.07 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 583.51 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1389.3 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.96 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 36.96 | m above nearest node |  | Tank Cost | € 683,393.46
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 336,449.00
|  |  |  | Total Investment Cost | € 1,927,347.80
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 315 | 190 | 48640
p10 | 100 | 200 | 315 | 190 | 38000
p11 | 80 | 111 | 160 | 52 | 5772
p12 | 80 | 106 | 160 | 52 | 5512
p13 | 80 | 215 | 160 | 52 | 11180
p16 | 25 | 168 | 75 | 17 | 2856
p18 | 100 | 420 | 225 | 100 | 42000
p19 | 100 | 459 | 225 | 100 | 45900
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a10
This sheet contains the results for tank connected to node: a10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.19 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 585.13 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1393.17 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.11 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 37.11 | m above nearest node |  | Tank Cost | € 684,038.01
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 329,133.00
|  |  |  | Total Investment Cost | € 1,920,676.34
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 315 | 190 | 48640
p11 | 80 | 111 | 315 | 190 | 21090
p12 | 80 | 106 | 225 | 100 | 10600
p13 | 80 | 215 | 225 | 100 | 21500
p15 | 80 | 386 | 90 | 21 | 8106
p16 | 25 | 168 | 90 | 21 | 3528
p18 | 100 | 420 | 200 | 79 | 33180
p19 | 100 | 459 | 225 | 100 | 45900
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a11
This sheet contains the results for tank connected to node: a11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.27 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | € 586.20 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1395.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.16 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 37.16 | m above nearest node |  | Tank Cost | € 684,250.30
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 363,666.00
|  |  |  | Total Investment Cost | € 1,955,421.64
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 315 | 190 | 48640
p10 | 100 | 200 | 225 | 100 | 20000
p11 | 80 | 111 | 250 | 120 | 13320
p12 | 80 | 106 | 315 | 190 | 20140
p13 | 80 | 215 | 250 | 120 | 25800
p14 | 80 | 369 | 90 | 21 | 7749
p16 | 25 | 168 | 90 | 21 | 3528
p18 | 100 | 420 | 225 | 100 | 42000
p19 | 100 | 459 | 225 | 100 | 45900
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a12
This sheet contains the results for tank connected to node: a12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.88 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | € 594.44 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1415.34 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.81 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 37.81 | m above nearest node |  | Tank Cost | € 687,130.08
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 410,725.00
|  |  |  | Total Investment Cost | € 2,005,360.41
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 315 | 190 | 48640
p10 | 100 | 200 | 140 | 41 | 8200
p11 | 80 | 111 | 315 | 190 | 21090
p12 | 80 | 106 | 200 | 79 | 8374
p13 | 80 | 215 | 90 | 21 | 4515
p14 | 80 | 369 | 315 | 190 | 70110
p15 | 80 | 386 | 200 | 79 | 30494
p16 | 25 | 168 | 200 | 79 | 13272
p18 | 100 | 420 | 200 | 79 | 33180
p19 | 100 | 459 | 200 | 79 | 36261
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a13
This sheet contains the results for tank connected to node: a13
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.09 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 597.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1421.57 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.93 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 37.93 | m above nearest node |  | Tank Cost | € 687,645.58
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 438,930.00
|  |  |  | Total Investment Cost | € 2,034,080.91
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 315 | 190 | 48640
p10 | 100 | 200 | 225 | 100 | 20000
p11 | 80 | 111 | 250 | 120 | 13320
p12 | 80 | 106 | 250 | 120 | 12720
p13 | 80 | 215 | 160 | 52 | 11180
p14 | 80 | 369 | 225 | 100 | 36900
p15 | 80 | 386 | 315 | 190 | 73340
p16 | 25 | 168 | 225 | 100 | 16800
p18 | 100 | 420 | 200 | 79 | 33180
p19 | 100 | 459 | 200 | 79 | 36261
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a14
This sheet contains the results for tank connected to node: a14
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.98 | m |  | Minimum Pressure | 20.03 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 569.03 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1354.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35.6 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 35.6 | m above nearest node |  | Tank Cost | € 677,395.58
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,747,945.91
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a15
This sheet contains the results for tank connected to node: a15
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.75 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | e05
Cost: | € 579.32 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1379.34 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.49 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 36.49 | m above nearest node |  | Tank Cost | € 681,327.98
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 331,633.00
|  |  |  | Total Investment Cost | € 1,920,466.31
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 250 | 120 | 30720
p10 | 100 | 200 | 225 | 100 | 20000
p11 | 80 | 111 | 125 | 34 | 3774
p12 | 80 | 106 | 110 | 28 | 2968
p13 | 80 | 215 | 110 | 28 | 6020
p16 | 25 | 168 | 63 | 14 | 2352
p18 | 100 | 420 | 225 | 100 | 42000
p19 | 100 | 459 | 315 | 190 | 87210
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a16
This sheet contains the results for tank connected to node: a16
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.79 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 566.42 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1348.61 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35.28 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 35.28 | m above nearest node |  | Tank Cost | € 675,983.70
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 163,045.00
|  |  |  | Total Investment Cost | € 1,746,534.04
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a17
This sheet contains the results for tank connected to node: a17
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.04 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | € 556.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1324.22 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 34.46 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 34.46 | m above nearest node |  | Tank Cost | € 672,388.26
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 245,969.00
|  |  |  | Total Investment Cost | € 1,825,862.59
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 315 | 190 | 31920
p22 | 80 | 291 | 125 | 34 | 9894
p24 | 80 | 255 | 200 | 79 | 20145
p25 | 50 | 206 | 125 | 34 | 7004
p26 | 100 | 202 | 200 | 79 | 15958
p27 | 80 | 289 | 125 | 34 | 9826
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a18
This sheet contains the results for tank connected to node: a18
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.57 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 563.10 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1340.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 34.88 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 34.88 | m above nearest node |  | Tank Cost | € 674,207.34
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 298,850.00
|  |  |  | Total Investment Cost | € 1,880,562.67
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 315 | 190 | 31920
p22 | 80 | 291 | 315 | 190 | 55290
p24 | 80 | 255 | 90 | 21 | 5355
p25 | 50 | 206 | 200 | 79 | 16274
p26 | 100 | 202 | 200 | 79 | 15958
p27 | 80 | 289 | 200 | 79 | 22831
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a19
This sheet contains the results for tank connected to node: a19
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.79 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 538.88 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1283.05 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 32.74 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 32.74 | m above nearest node |  | Tank Cost | € 664,798.11
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 233,089.00
|  |  |  | Total Investment Cost | € 1,805,392.44
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p23 | 300 | 295 | 355 | 240 | 70800
p24 | 80 | 255 | 90 | 21 | 5355
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a20
This sheet contains the results for tank connected to node: a20
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.59 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | € 549.76 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1308.96 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 33.65 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 33.65 | m above nearest node |  | Tank Cost | € 668,814.71
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 303,896.00
|  |  |  | Total Investment Cost | € 1,880,216.05
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 250 | 120 | 20160
p22 | 80 | 291 | 125 | 34 | 9894
p23 | 300 | 295 | 315 | 190 | 56050
p24 | 80 | 255 | 225 | 100 | 25500
p25 | 50 | 206 | 125 | 34 | 7004
p26 | 100 | 202 | 250 | 120 | 24240
p27 | 80 | 289 | 125 | 34 | 9826
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## a21
This sheet contains the results for tank connected to node: a21
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.96 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | € 554.80 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1320.96 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 34.03 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 34.03 | m above nearest node |  | Tank Cost | € 670,472.17
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 366,737.00
|  |  |  | Total Investment Cost | € 1,944,714.50
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 250 | 120 | 20160
p22 | 80 | 291 | 225 | 100 | 29100
p23 | 300 | 295 | 315 | 190 | 56050
p24 | 80 | 255 | 140 | 41 | 10455
p25 | 50 | 206 | 225 | 100 | 20600
p26 | 100 | 202 | 250 | 120 | 24240
p27 | 80 | 289 | 315 | 190 | 54910
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b01
This sheet contains the results for tank connected to node: b01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.66 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | € 510.07 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1214.45 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.11 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 30.11 | m above nearest node |  | Tank Cost | € 653,204.09
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 322,369.00
|  |  |  | Total Investment Cost | € 1,883,078.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p23 | 300 | 295 | 355 | 240 | 70800
p24 | 80 | 255 | 90 | 21 | 5355
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b02
This sheet contains the results for tank connected to node: b02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.11 | m |  | Minimum Pressure | 20.07 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 515.89 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1228.31 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.25 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 30.25 | m above nearest node |  | Tank Cost | € 653,806.02
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 393,809.00
|  |  |  | Total Investment Cost | € 1,955,120.35
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p23 | 300 | 295 | 355 | 240 | 70800
p24 | 80 | 255 | 90 | 21 | 5355
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b03
This sheet contains the results for tank connected to node: b03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.39 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | € 519.47 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1236.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.41 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 30.41 | m above nearest node |  | Tank Cost | € 654,512.62
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 441,685.00
|  |  |  | Total Investment Cost | € 2,003,702.96
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b04
This sheet contains the results for tank connected to node: b04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.86 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 525.60 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1251.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.73 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 30.73 | m above nearest node |  | Tank Cost | € 655,917.94
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 499,942.00
|  |  |  | Total Investment Cost | € 2,063,365.27
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p31 | 150 | 278 | 315 | 190 | 52820
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 90 | 21 | 6090
p36 | 50 | 269 | 90 | 21 | 5649
p37 | 50 | 333 | 90 | 21 | 6993
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b05
This sheet contains the results for tank connected to node: b05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.29 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | € 531.13 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1264.59 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.14 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 31.14 | m above nearest node |  | Tank Cost | € 657,716.00
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 570,414.00
|  |  |  | Total Investment Cost | € 2,135,635.33
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p31 | 150 | 278 | 315 | 190 | 52820
p32 | 125 | 270 | 315 | 190 | 51300
p33 | 80 | 106 | 125 | 34 | 3604
p34 | 50 | 290 | 110 | 28 | 8120
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 110 | 28 | 7532
p37 | 50 | 333 | 110 | 28 | 9324
p38 | 80 | 380 | 110 | 28 | 10640
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b06
This sheet contains the results for tank connected to node: b06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.12 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | € 528.91 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1259.32 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 31 | m above nearest node |  | Tank Cost | € 657,107.38
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 525,241.00
|  |  |  | Total Investment Cost | € 2,089,853.71
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p33 | 80 | 106 | 125 | 34 | 3604
p34 | 50 | 290 | 110 | 28 | 8120
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 125 | 34 | 11322
p38 | 80 | 380 | 110 | 28 | 10640
p39 | 125 | 380 | 315 | 190 | 72200
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b07
This sheet contains the results for tank connected to node: b07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.22 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | € 530.30 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1262.63 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.1 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 31.1 | m above nearest node |  | Tank Cost | € 657,557.02
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 567,187.00
|  |  |  | Total Investment Cost | € 2,132,249.35
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p24 | 80 | 255 | 90 | 21 | 5355
p25 | 50 | 206 | 63 | 14 | 2884
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p32 | 125 | 270 | 140 | 41 | 11070
p33 | 80 | 106 | 315 | 190 | 20140
p34 | 50 | 290 | 140 | 41 | 11890
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 140 | 41 | 13653
p38 | 80 | 380 | 110 | 28 | 10640
p39 | 125 | 380 | 315 | 190 | 72200
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b08
This sheet contains the results for tank connected to node: b08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.32 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.83 | L/s |  | Critical Node | e05
Cost: | € 544.79 | Euro per day |  | Critical Pipes | ['p38'] | Unit headloss >10m/km
Energy: | 1297.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.98 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 31.98 | m above nearest node |  | Tank Cost | € 661,434.48
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 612,291.00
|  |  |  | Total Investment Cost | € 2,181,230.82
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p31 | 150 | 278 | 225 | 100 | 27800
p32 | 125 | 270 | 225 | 100 | 27000
p33 | 80 | 106 | 250 | 120 | 12720
p34 | 50 | 290 | 250 | 120 | 34800
p36 | 50 | 269 | 90 | 21 | 5649
p37 | 50 | 333 | 225 | 100 | 33300
p38 | 80 | 380 | 110 | 28 | 10640
p39 | 125 | 380 | 250 | 120 | 45600
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b09
This sheet contains the results for tank connected to node: b09
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.05 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | € 528.07 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1257.3 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.97 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 30.97 | m above nearest node |  | Tank Cost | € 656,964.98
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 514,126.00
|  |  |  | Total Investment Cost | € 2,078,596.31
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 110 | 28 | 7532
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 125 | 34 | 12920
p40 | 125 | 289 | 315 | 190 | 54910
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b10
This sheet contains the results for tank connected to node: b10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.24 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | € 530.54 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1263.18 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.16 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 31.16 | m above nearest node |  | Tank Cost | € 657,811.21
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 535,406.00
|  |  |  | Total Investment Cost | € 2,100,722.54
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 110 | 28 | 7532
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 125 | 34 | 12920
p40 | 125 | 289 | 315 | 190 | 54910
p41 | 125 | 112 | 315 | 190 | 21280
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b11
This sheet contains the results for tank connected to node: b11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.67 | m |  | Minimum Pressure | 19.98 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | € 536.21 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1276.69 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.44 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 31.44 | m above nearest node |  | Tank Cost | € 659,054.90
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 650,185.00
|  |  |  | Total Investment Cost | € 2,216,745.23
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p31 | 150 | 278 | 160 | 52 | 14456
p32 | 125 | 270 | 160 | 52 | 14040
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 75 | 17 | 4930
p35 | 100 | 439 | 315 | 190 | 83410
p36 | 50 | 269 | 160 | 52 | 13988
p37 | 50 | 333 | 75 | 17 | 5661
p38 | 80 | 380 | 160 | 52 | 19760
p40 | 125 | 289 | 315 | 190 | 54910
p41 | 125 | 112 | 315 | 190 | 21280
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## b12
This sheet contains the results for tank connected to node: b12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.29 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | e05
Cost: | € 570.82 | Euro per day |  | Critical Pipes | ['p37'] | Unit headloss >10m/km
Energy: | 1359.08 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 32.87 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 32.87 | m above nearest node |  | Tank Cost | € 665,347.51
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 594,380.00
|  |  |  | Total Investment Cost | € 2,167,232.84
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p29 | 200 | 376 | 315 | 190 | 71440
p30 | 200 | 248 | 315 | 190 | 47120
p31 | 150 | 278 | 250 | 120 | 33360
p32 | 125 | 270 | 250 | 120 | 32400
p33 | 80 | 106 | 90 | 21 | 2226
p34 | 50 | 290 | 90 | 21 | 6090
p35 | 100 | 439 | 200 | 79 | 34681
p36 | 50 | 269 | 200 | 79 | 21251
p37 | 50 | 333 | 75 | 17 | 5661
p38 | 80 | 380 | 250 | 120 | 45600
p40 | 125 | 289 | 200 | 79 | 22831
p41 | 125 | 112 | 200 | 79 | 8848
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## c01
This sheet contains the results for tank connected to node: c01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.77 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b08
Cost: | € 470.44 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1120.1 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.58 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 26.58 | m above nearest node |  | Tank Cost | € 637,606.68
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 502,778.00
|  |  |  | Total Investment Cost | € 2,047,890.01
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 355 | 240 | 174480
p54 | 80 | 177 | 90 | 21 | 3717
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## c02
This sheet contains the results for tank connected to node: c02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.57 | m |  | Minimum Pressure | 20.02 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b08
Cost: | € 480.85 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1144.88 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.77 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 26.77 | m above nearest node |  | Tank Cost | € 638,459.81
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 531,020.00
|  |  |  | Total Investment Cost | € 2,076,985.14
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p53 | 100 | 177 | 110 | 28 | 4956
p54 | 80 | 177 | 110 | 28 | 4956
p55 | 80 | 159 | 110 | 28 | 4452
p56 | 100 | 349 | 125 | 34 | 11866
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## c03
This sheet contains the results for tank connected to node: c03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.86 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | b08
Cost: | € 484.61 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1153.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.05 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.05 | m above nearest node |  | Tank Cost | € 639,708.34
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 591,995.00
|  |  |  | Total Investment Cost | € 2,139,208.67
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p53 | 100 | 177 | 315 | 190 | 33630
p54 | 80 | 177 | 160 | 52 | 9204
p55 | 80 | 159 | 160 | 52 | 8268
p56 | 100 | 349 | 200 | 79 | 27571
p57 | 125 | 108 | 200 | 79 | 8532
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## c04
This sheet contains the results for tank connected to node: c04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | b08
Cost: | € 486.38 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1158.06 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.18 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.18 | m above nearest node |  | Tank Cost | € 640,275.96
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 628,400.00
|  |  |  | Total Investment Cost | € 2,176,181.30
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p53 | 100 | 177 | 315 | 190 | 33630
p54 | 80 | 177 | 315 | 190 | 33630
p55 | 80 | 159 | 200 | 79 | 12561
p56 | 100 | 349 | 200 | 79 | 27571
p57 | 125 | 108 | 200 | 79 | 8532
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 225 | 100 | 36600
p69 | 150 | 452 | 160 | 52 | 23504

## c05
This sheet contains the results for tank connected to node: c05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.94 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | b08
Cost: | € 485.50 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1155.96 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.92 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 26.92 | m above nearest node |  | Tank Cost | € 639,117.45
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 577,724.00
|  |  |  | Total Investment Cost | € 2,124,346.79
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 160 | 52 | 9568
p53 | 100 | 177 | 140 | 41 | 7257
p54 | 80 | 177 | 140 | 41 | 7257
p55 | 80 | 159 | 140 | 41 | 6519
p56 | 100 | 349 | 125 | 34 | 11866
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 315 | 190 | 69540
p69 | 150 | 452 | 160 | 52 | 23504

## c06
This sheet contains the results for tank connected to node: c06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.02 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b08
Cost: | € 499.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1189.99 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27 | m above nearest node |  | Tank Cost | € 639,476.87
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 569,284.00
|  |  |  | Total Investment Cost | € 2,116,266.20
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 160 | 52 | 9568
p53 | 100 | 177 | 160 | 52 | 9204
p54 | 80 | 177 | 140 | 41 | 7257
p55 | 80 | 159 | 140 | 41 | 6519
p56 | 100 | 349 | 140 | 41 | 14309
p57 | 125 | 108 | 315 | 190 | 20520
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 315 | 190 | 69540
p69 | 150 | 452 | 160 | 52 | 23504

## c07
This sheet contains the results for tank connected to node: c07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.74 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | b08
Cost: | € 509.25 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1212.49 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.82 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.82 | m above nearest node |  | Tank Cost | € 643,113.37
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 580,826.00
|  |  |  | Total Investment Cost | € 2,131,444.71
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 250 | 120 | 22080
p53 | 100 | 177 | 250 | 120 | 21240
p54 | 80 | 177 | 250 | 120 | 21240
p55 | 80 | 159 | 250 | 120 | 19080
p56 | 100 | 349 | 225 | 100 | 34900
p57 | 125 | 108 | 225 | 100 | 10800
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 250 | 120 | 43920
p69 | 150 | 452 | 160 | 52 | 23504

## d01
This sheet contains the results for tank connected to node: d01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.54 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | b08
Cost: | € 480.44 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1143.91 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.21 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.21 | m above nearest node |  | Tank Cost | € 640,393.26
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 598,510.00
|  |  |  | Total Investment Cost | € 2,146,408.60
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 355 | 240 | 174480
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p54 | 80 | 177 | 110 | 28 | 4956
p55 | 80 | 159 | 110 | 28 | 4452
p56 | 100 | 349 | 110 | 28 | 9772
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d02
This sheet contains the results for tank connected to node: d02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.5 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | b08
Cost: | € 506.28 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1205.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.72 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.72 | m above nearest node |  | Tank Cost | € 642,636.81
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 557,346.00
|  |  |  | Total Investment Cost | € 2,107,488.14
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p45 | 50 | 214 | 315 | 190 | 40660
p54 | 80 | 177 | 90 | 21 | 3717
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d03
This sheet contains the results for tank connected to node: d03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.61 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.82 | L/s |  | Critical Node | b08
Cost: | € 494.42 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1177.2 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.6 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.6 | m above nearest node |  | Tank Cost | € 642,140.34
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 581,206.00
|  |  |  | Total Investment Cost | € 2,130,851.67
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p46 | 150 | 195 | 315 | 190 | 37050
p54 | 80 | 177 | 110 | 28 | 4956
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d04
This sheet contains the results for tank connected to node: d04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.21 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | b12
Cost: | € 515.51 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1227.4 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.45 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 28.45 | m above nearest node |  | Tank Cost | € 645,850.51
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 685,617.00
|  |  |  | Total Investment Cost | € 2,238,972.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p46 | 150 | 195 | 315 | 190 | 37050
p47 | 100 | 136 | 200 | 79 | 10744
p48 | 80 | 461 | 315 | 190 | 87590
p49 | 50 | 148 | 160 | 52 | 7696
p50 | 100 | 85 | 200 | 79 | 6715
p51 | 50 | 368 | 160 | 52 | 19136
p54 | 80 | 177 | 90 | 21 | 3717
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d05
This sheet contains the results for tank connected to node: d05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.85 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.8 | L/s |  | Critical Node | b08
Cost: | € 497.63 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1184.82 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.87 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.87 | m above nearest node |  | Tank Cost | € 643,305.95
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 648,524.00
|  |  |  | Total Investment Cost | € 2,199,335.28
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p46 | 150 | 195 | 315 | 190 | 37050
p47 | 100 | 136 | 315 | 190 | 25840
p48 | 80 | 461 | 125 | 34 | 15674
p49 | 50 | 148 | 125 | 34 | 5032
p50 | 100 | 85 | 110 | 28 | 2380
p51 | 50 | 368 | 125 | 34 | 12512
p54 | 80 | 177 | 90 | 21 | 3717
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d06
This sheet contains the results for tank connected to node: d06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.02 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | b12
Cost: | € 499.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1189.99 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.04 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 28.04 | m above nearest node |  | Tank Cost | € 644,062.48
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 665,521.00
|  |  |  | Total Investment Cost | € 2,217,088.81
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p46 | 150 | 195 | 315 | 190 | 37050
p47 | 100 | 136 | 315 | 190 | 25840
p48 | 80 | 461 | 140 | 41 | 18901
p49 | 50 | 148 | 125 | 34 | 5032
p50 | 100 | 85 | 315 | 190 | 16150
p51 | 50 | 368 | 125 | 34 | 12512
p54 | 80 | 177 | 90 | 21 | 3717
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d07
This sheet contains the results for tank connected to node: d07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.08 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.85 | L/s |  | Critical Node | b12
Cost: | € 540.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1286.73 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.1 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 30.1 | m above nearest node |  | Tank Cost | € 653,134.20
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 666,417.00
|  |  |  | Total Investment Cost | € 2,227,056.53
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p46 | 150 | 195 | 315 | 190 | 37050
p47 | 100 | 136 | 225 | 100 | 13600
p48 | 80 | 461 | 225 | 100 | 46100
p49 | 50 | 148 | 225 | 100 | 14800
p50 | 100 | 85 | 225 | 100 | 8500
p51 | 50 | 368 | 225 | 100 | 36800
p54 | 80 | 177 | 90 | 21 | 3717
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## d08
This sheet contains the results for tank connected to node: d08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.86 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | € 510.87 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1216.36 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.88 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 28.88 | m above nearest node |  | Tank Cost | € 647,770.04
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 702,496.00
|  |  |  | Total Investment Cost | € 2,257,771.38
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p43 | 150 | 184 | 315 | 190 | 34960
p44 | 150 | 201 | 315 | 190 | 38190
p46 | 150 | 195 | 315 | 190 | 37050
p47 | 100 | 136 | 315 | 190 | 25840
p48 | 80 | 461 | 110 | 28 | 12908
p49 | 50 | 148 | 110 | 28 | 4144
p50 | 100 | 85 | 315 | 190 | 16150
p51 | 50 | 368 | 90 | 21 | 7728
p52 | 80 | 256 | 315 | 190 | 48640
p54 | 80 | 177 | 90 | 21 | 3717
p55 | 80 | 159 | 90 | 21 | 3339
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e01
This sheet contains the results for tank connected to node: e01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.88 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b08
Cost: | € 471.90 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1123.57 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.59 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 26.59 | m above nearest node |  | Tank Cost | € 637,652.08
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 546,906.00
|  |  |  | Total Investment Cost | € 2,092,063.41
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 355 | 240 | 174480
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 355 | 240 | 40320
p59 | 150 | 361 | 200 | 79 | 28519
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e02
This sheet contains the results for tank connected to node: e02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.79 | m |  | Minimum Pressure | 19.94 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b08
Cost: | € 496.74 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1182.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.76 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 26.76 | m above nearest node |  | Tank Cost | € 638,413.00
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 508,877.00
|  |  |  | Total Investment Cost | € 2,054,795.33
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e03
This sheet contains the results for tank connected to node: e03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.34 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | b08
Cost: | € 503.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1199.61 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.27 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.27 | m above nearest node |  | Tank Cost | € 640,658.65
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 571,627.00
|  |  |  | Total Investment Cost | € 2,119,790.98
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p60 | 150 | 289 | 315 | 190 | 54910
p66 | 50 | 280 | 110 | 28 | 7840
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e04
This sheet contains the results for tank connected to node: e04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.82 | m |  | Minimum Pressure | 19.97 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | € 510.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1214.7 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.59 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.59 | m above nearest node |  | Tank Cost | € 642,088.19
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 637,809.00
|  |  |  | Total Investment Cost | € 2,187,402.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p60 | 150 | 289 | 315 | 190 | 54910
p61 | 125 | 277 | 315 | 190 | 52630
p65 | 80 | 272 | 110 | 28 | 7616
p66 | 50 | 280 | 90 | 21 | 5880
p67 | 50 | 282 | 110 | 28 | 7896
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e05
This sheet contains the results for tank connected to node: e05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.63 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | b12
Cost: | € 520.81 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1240.03 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.48 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 28.48 | m above nearest node |  | Tank Cost | € 645,989.74
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 685,878.00
|  |  |  | Total Investment Cost | € 2,239,373.08
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p60 | 150 | 289 | 315 | 190 | 54910
p61 | 125 | 277 | 315 | 190 | 52630
p62 | 80 | 266 | 315 | 190 | 50540
p66 | 50 | 280 | 90 | 21 | 5880
p67 | 50 | 282 | 90 | 21 | 5922
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e06
This sheet contains the results for tank connected to node: e06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.69 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | b08
Cost: | € 495.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1179.22 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.49 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.49 | m above nearest node |  | Tank Cost | € 641,657.77
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 661,233.00
|  |  |  | Total Investment Cost | € 2,210,396.10
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p60 | 150 | 289 | 160 | 52 | 15028
p63 | 100 | 354 | 315 | 190 | 67260
p64 | 100 | 325 | 140 | 41 | 13325
p66 | 50 | 280 | 140 | 41 | 11480
p67 | 50 | 282 | 75 | 17 | 4794
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e07
This sheet contains the results for tank connected to node: e07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.64 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | b12
Cost: | € 521.11 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1240.74 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.36 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 28.36 | m above nearest node |  | Tank Cost | € 645,469.93
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 676,945.00
|  |  |  | Total Investment Cost | € 2,229,920.26
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p60 | 150 | 289 | 315 | 190 | 54910
p61 | 125 | 277 | 140 | 41 | 11357
p63 | 100 | 354 | 160 | 52 | 18408
p64 | 100 | 325 | 250 | 120 | 39000
p65 | 80 | 272 | 140 | 41 | 11152
p66 | 50 | 280 | 160 | 52 | 14560
p67 | 50 | 282 | 140 | 41 | 11562
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## e08
This sheet contains the results for tank connected to node: e08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.06 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | b12
Cost: | € 526.51 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1253.59 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.8 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 28.8 | m above nearest node |  | Tank Cost | € 647,400.55
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 706,295.00
|  |  |  | Total Investment Cost | € 2,261,200.88
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 125 | 34 | 5712
p22 | 80 | 291 | 90 | 21 | 6111
p23 | 300 | 295 | 315 | 190 | 56050
p28 | 300 | 372 | 315 | 190 | 70680
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p54 | 80 | 177 | 90 | 21 | 3717
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 315 | 190 | 68590
p60 | 150 | 289 | 315 | 190 | 54910
p61 | 125 | 277 | 250 | 120 | 33240
p63 | 100 | 354 | 125 | 34 | 12036
p64 | 100 | 325 | 200 | 79 | 25675
p65 | 80 | 272 | 250 | 120 | 32640
p66 | 50 | 280 | 125 | 34 | 9520
p67 | 50 | 282 | 200 | 79 | 22278
p68 | 150 | 366 | 200 | 79 | 28914
p69 | 150 | 452 | 160 | 52 | 23504

## f01
This sheet contains the results for tank connected to node: f01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.78 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b08
Cost: | € 496.40 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1181.9 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.45 | m above sea level |  | Pump Cost | € 907,505.33
Tank height above ground | 27.45 | m above nearest node |  | Tank Cost | € 641,445.31
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | € 649,697.00
|  |  |  | Total Investment Cost | € 2,198,647.65
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
p03 | 80 | 380 | 90 | 21 | 7980
p07 | 80 | 249 | 90 | 21 | 5229
p09 | 100 | 256 | 140 | 41 | 10496
p11 | 80 | 111 | 110 | 28 | 3108
p19 | 100 | 459 | 110 | 28 | 12852
p21 | 100 | 168 | 110 | 28 | 4704
p23 | 300 | 295 | 355 | 240 | 70800
p28 | 300 | 372 | 355 | 240 | 89280
p33 | 80 | 106 | 110 | 28 | 2968
p34 | 50 | 290 | 63 | 14 | 4060
p35 | 100 | 439 | 110 | 28 | 12292
p36 | 50 | 269 | 75 | 17 | 4573
p37 | 50 | 333 | 63 | 14 | 4662
p38 | 80 | 380 | 110 | 28 | 10640
p42 | 250 | 727 | 315 | 190 | 138130
p47 | 100 | 136 | 110 | 28 | 3808
p53 | 100 | 177 | 125 | 34 | 6018
p54 | 80 | 177 | 125 | 34 | 6018
p55 | 80 | 159 | 125 | 34 | 5406
p56 | 100 | 349 | 125 | 34 | 11866
p58 | 250 | 168 | 315 | 190 | 31920
p59 | 150 | 361 | 200 | 79 | 28519
p60 | 150 | 289 | 160 | 52 | 15028
p66 | 50 | 280 | 63 | 14 | 3920
p68 | 150 | 366 | 315 | 190 | 69540
p69 | 150 | 452 | 315 | 190 | 85880