## Summary
Summary of results for tank connected to each node
Column1 | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
0 | J65 | 5.91 | 142.94 | 71.22 | 71.22 | 1341.9 | 3195 | 332.2 | 322.2 | 804.56 | 20.1 | 22 | R_TIBAR_2 | [] | 676560.33 | 1198371.53 | 1285976.51 | 3160908.37 | 32149.77 | 275582.4 | 797526.37
1 | J66 | 5.13 | 142.21 | 71.22 | 71.23 | 1335.11 | 3178.83 | 333.99 | 303.99 | 804.56 | 20.1 | 22 | R_TIBAR_2 | [] | 676560.33 | 1154409.73 | 956240.38 | 2787210.45 | 30149.4 | 243001.71 | 760466.01
2 | J67 | 5.64 | 142.31 | 71.22 | 71.22 | 1335.96 | 3180.86 | 333.87 | 323.87 | 804.56 | 20.1 | 22 | R_TIBAR_2 | [] | 676560.33 | 1202415.31 | 1278530.21 | 3157505.85 | 32144.89 | 275285.75 | 795056.75
3 | J69 | 8.09 | 142.92 | 71.22 | 71.24 | 1341.76 | 3194.66 | 334.03 | 214.03 | 804.56 | 20.09 | 23 | R_TIBAR_2 | [] | 676560.33 | 937278.6 | 815244 | 2429082.94 | 27707.37 | 211778.52 | 729227.16
4 | J70 | 6.01 | 142.32 | 71.22 | 71.23 | 1336.04 | 3181.05 | 334.03 | 324.03 | 804.56 | 20.1 | 22 | R_TIBAR_2 | [] | 676560.33 | 1202790.61 | 1411735.73 | 3291086.67 | 32813.92 | 286931.93 | 807400.68
5 | J71 | 5.35 | 142.26 | 71.22 | 71.23 | 1335.56 | 3179.91 | 334.08 | 324.08 | 804.56 | 20.1 | 22 | R_TIBAR_2 | [] | 676560.33 | 1202904.41 | 1186187.27 | 3065652.02 | 31687.09 | 267277.51 | 786444.78
6 | J72 | 4.9 | 142.26 | 71.22 | 71.24 | 1335.57 | 3179.93 | 334.32 | 304.32 | 804.56 | 20.1 | 22 | R_TIBAR_2 | [] | 676560.33 | 1155216.83 | 910742.08 | 2742519.24 | 29928.36 | 239105.32 | 756516.55
7 | J73 | 4.63 | 142.26 | 71.22 | 71.24 | 1335.5 | 3179.75 | 334.44 | 304.44 | 804.56 | 20.1 | 23 | R_TIBAR_2 | [] | 676560.33 | 1155517.95 | 731954.3 | 2564032.58 | 29036.83 | 223544.04 | 740037.11
8 | J139 | 3.18 | 142.91 | 71.22 | 71.24 | 1341.64 | 3194.39 | 334.04 | 254.04 | 804.56 | 20.09 | 23 | R_TIBAR_2 | [] | 676560.33 | 1033855.68 | 694344 | 2404760.02 | 27875.49 | 209657.94 | 727233.12
9 | TIBAR_PORT | 6.41 | 142.41 | 71.22 | 71.22 | 1336.87 | 3183.02 | 333.87 | 323.87 | 804.56 | 20.09 | 22 | R_TIBAR_2 | [] | 676560.33 | 1202397.12 | 1529820.07 | 3408777.52 | 33401.2 | 297192.76 | 818551.52
10 | R_TIBAR_2 | 1.05 | 146.58 | 71.22 | 71.24 | 1376.11 | 3276.44 | 338.09 | 18.09 | 804.56 | 20.09 | 23 | R_TIBAR_2 | [] | 676560.33 | 464357.87 | 392958 | 1533876.21 | 21812.57 | 133730.32 | 657821.4
11 | R_TIBAR_3 | 2.63 | 142.93 | 71.22 | 71.24 | 1341.81 | 3194.79 | 334.55 | 174.55 | 804.56 | 20.1 | 23 | R_TIBAR_2 | [] | 676560.33 | 841993.37 | 694344 | 2212897.71 | 26340.59 | 192930.51 | 709031.81
12 | R_TIBAR_4 | 2.66 | 142.93 | 71.22 | 71.24 | 1341.78 | 3194.71 | 334.53 | 174.53 | 804.56 | 20.1 | 23 | R_TIBAR_2 | [] | 676560.33 | 841934.74 | 694344 | 2212839.07 | 26340.12 | 192925.39 | 709014.03
13 | ETA_COMORO | 0 | 145.13 | 71.22 | 71.24 | 1362.46 | 3243.95 | 341.58 | 241.58 | 804.56 | 20.1 | 21 | R_TIBAR_2 | [] | 676560.33 | 1003779.16 | 549689 | 2230028.49 | 26911.6 | 194424.05 | 718633.11
14 | R_TIBAR_1 | 1 | 146.38 | 71.22 | 71.24 | 1374.21 | 3271.92 | 338.25 | 18.25 | 804.56 | 20.1 | 23 | R_TIBAR_2 | [] | 676560.33 | 464733.54 | 404358 | 1545651.87 | 21872.58 | 134756.97 | 658215.24
15 | prv2 | 3.18 | 142.91 | 71.22 | 71.24 | 1341.64 | 3194.39 | 334.04 | 254.04 | 804.56 | 20.09 | 23 | R_TIBAR_2 | [] | 676560.33 | 1033856.79 | 694344 | 2404761.12 | 27875.49 | 209658.03 | 727233.73
16 | prv3 | 4.63 | 142.26 | 71.22 | 71.24 | 1335.49 | 3179.75 | 334.44 | 304.44 | 804.56 | 20.1 | 23 | R_TIBAR_2 | [] | 676560.33 | 1155519.79 | 731954.3 | 2564034.42 | 29036.85 | 223544.21 | 740036.39
1

## J65
This sheet contains the results for tank connected to node: J65
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.94 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.22 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,341.90 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3195 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 332.2 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 322.2 | m above nearest node |  | Tank Cost | € 1,198,371.53
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,285,976.51
|  |  |  | Total Investment Cost | € 3,160,908.37
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 200 | 79 | 29895.97
P25 | 54.9 | 894.02 | 160 | 52 | 46489.04
P27 | 110.2 | 622.86 | 160 | 52 | 32388.72
P28 | 54.9 | 793.82 | 200 | 79 | 62711.78
P29 | 123.4 | 733.42 | 315 | 190 | 139349.8
P30 | 198.2 | 903.77 | 315 | 190 | 171716.3
P31 | 220.4 | 574.11 | 315 | 190 | 109080.9
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400

## J66
This sheet contains the results for tank connected to node: J66
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.21 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.23 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,335.11 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3178.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 333.99 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 303.99 | m above nearest node |  | Tank Cost | € 1,154,409.73
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 956,240.38
|  |  |  | Total Investment Cost | € 2,787,210.45
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P25 | 54.9 | 894.02 | 75 | 17 | 15198.34
P28 | 54.9 | 793.82 | 75 | 17 | 13494.94
P32 | 277.6 | 814.97 | 355 | 240 | 195592.8
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180

## J67
This sheet contains the results for tank connected to node: J67
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.31 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.22 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,335.96 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3180.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 333.87 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 323.87 | m above nearest node |  | Tank Cost | € 1,202,415.31
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,278,530.21
|  |  |  | Total Investment Cost | € 3,157,505.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 90 | 21 | 7947.03
P25 | 54.9 | 894.02 | 140 | 41 | 36654.82
P26 | 176.2 | 1028.22 | 355 | 240 | 246772.8
P27 | 110.2 | 622.86 | 125 | 34 | 21177.24
P28 | 54.9 | 793.82 | 75 | 17 | 13494.94
P29 | 123.4 | 733.42 | 125 | 34 | 24936.28
P32 | 277.6 | 814.97 | 355 | 240 | 195592.8
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180

## J69
This sheet contains the results for tank connected to node: J69
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.92 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,341.76 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3194.66 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.03 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 214.03 | m above nearest node |  | Tank Cost | € 937,278.60
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 815,244.00
|  |  |  | Total Investment Cost | € 2,429,082.94
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P171 | 54.9 | 503.75 | 355 | 240 | 120900
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400

## J70
This sheet contains the results for tank connected to node: J70
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.32 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.23 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,336.04 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3181.05 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.03 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 324.03 | m above nearest node |  | Tank Cost | € 1,202,790.61
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,411,735.73
|  |  |  | Total Investment Cost | € 3,291,086.67
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 200 | 79 | 29895.97
P25 | 54.9 | 894.02 | 160 | 52 | 46489.04
P27 | 110.2 | 622.86 | 355 | 240 | 149486.4
P28 | 54.9 | 793.82 | 160 | 52 | 41278.64
P29 | 123.4 | 733.42 | 200 | 79 | 57940.18
P30 | 198.2 | 903.77 | 355 | 240 | 216904.8
P31 | 220.4 | 574.11 | 355 | 240 | 137786.4
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180

## J71
This sheet contains the results for tank connected to node: J71
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.26 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.23 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,335.56 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3179.91 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.08 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 324.08 | m above nearest node |  | Tank Cost | € 1,202,904.41
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,186,187.27
|  |  |  | Total Investment Cost | € 3,065,652.02
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 75 | 17 | 6433.31
P25 | 54.9 | 894.02 | 125 | 34 | 30396.68
P28 | 54.9 | 793.82 | 200 | 79 | 62711.78
P30 | 198.2 | 903.77 | 355 | 240 | 216904.8
P31 | 220.4 | 574.11 | 355 | 240 | 137786.4
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180

## J72
This sheet contains the results for tank connected to node: J72
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.26 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,335.57 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3179.93 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.32 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 304.32 | m above nearest node |  | Tank Cost | € 1,155,216.83
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 910,742.08
|  |  |  | Total Investment Cost | € 2,742,519.24
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P25 | 54.9 | 894.02 | 90 | 21 | 18774.42
P28 | 54.9 | 793.82 | 110 | 28 | 22226.96
P31 | 220.4 | 574.11 | 355 | 240 | 137786.4
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180

## J73
This sheet contains the results for tank connected to node: J73
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.26 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,335.50 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3179.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.44 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 304.44 | m above nearest node |  | Tank Cost | € 1,155,517.95
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 731,954.30
|  |  |  | Total Investment Cost | € 2,564,032.58
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180

## J139
This sheet contains the results for tank connected to node: J139
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.91 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,341.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3194.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.04 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 254.04 | m above nearest node |  | Tank Cost | € 1,033,855.68
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 694,344.00
|  |  |  | Total Investment Cost | € 2,404,760.02
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400

## TIBAR_PORT
This sheet contains the results for tank connected to node: TIBAR_PORT
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.41 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 71.22 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,336.87 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3183.02 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 333.87 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 323.87 | m above nearest node |  | Tank Cost | € 1,202,397.12
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 1,529,820.07
|  |  |  | Total Investment Cost | € 3,408,777.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P24 | 54.9 | 378.43 | 90 | 21 | 7947.03
P25 | 54.9 | 894.02 | 140 | 41 | 36654.82
P26 | 176.2 | 1028.22 | 355 | 240 | 246772.8
P27 | 110.2 | 622.86 | 125 | 34 | 21177.24
P29 | 123.4 | 733.42 | 125 | 34 | 24936.28
P32 | 277.6 | 814.97 | 355 | 240 | 195592.8
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
P176 | 123.4 | 1103.27 | 355 | 240 | 264784.8
1 | 277.6 | 60 | 400 | 253 | 15180

## R_TIBAR_2
This sheet contains the results for tank connected to node: R_TIBAR_2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 146.58 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,376.11 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3276.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 338.09 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 18.09 | m above nearest node |  | Tank Cost | € 464,357.87
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 392,958.00
|  |  |  | Total Investment Cost | € 1,533,876.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958

## R_TIBAR_3
This sheet contains the results for tank connected to node: R_TIBAR_3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.93 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,341.81 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3194.79 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.55 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 174.55 | m above nearest node |  | Tank Cost | € 841,993.37
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 694,344.00
|  |  |  | Total Investment Cost | € 2,212,897.71
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400

## R_TIBAR_4
This sheet contains the results for tank connected to node: R_TIBAR_4
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.93 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,341.78 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3194.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.53 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 174.53 | m above nearest node |  | Tank Cost | € 841,934.74
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 694,344.00
|  |  |  | Total Investment Cost | € 2,212,839.07
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400

## ETA_COMORO
This sheet contains the results for tank connected to node: ETA_COMORO
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 145.13 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,362.46 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3243.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 341.58 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 241.58 | m above nearest node |  | Tank Cost | € 1,003,779.16
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 549,689.00
|  |  |  | Total Investment Cost | € 2,230,028.49
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
P175 | 277.6 | 764.9 | 315 | 190 | 145331
1 | 277.6 | 60 | 315 | 190 | 11400

## R_TIBAR_1
This sheet contains the results for tank connected to node: R_TIBAR_1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 146.38 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,374.21 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3271.92 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 338.25 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 18.25 | m above nearest node |  | Tank Cost | € 464,733.54
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 404,358.00
|  |  |  | Total Investment Cost | € 1,545,651.87
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 315 | 190 | 392958
1 | 277.6 | 60 | 315 | 190 | 11400

## prv2
This sheet contains the results for tank connected to node: prv2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.91 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,341.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3194.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.04 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 254.04 | m above nearest node |  | Tank Cost | € 1,033,856.79
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 694,344.00
|  |  |  | Total Investment Cost | € 2,404,761.12
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 355 | 240 | 496368
P175 | 277.6 | 764.9 | 355 | 240 | 183576
1 | 277.6 | 60 | 355 | 240 | 14400

## prv3
This sheet contains the results for tank connected to node: prv3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 142.26 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 71.22 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 71.24 | L/s |  | Critical Node | R_TIBAR_2
Cost: | € 1,335.49 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 3179.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 334.44 | m above sea level |  | Pump Cost | € 676,560.33
Tank height above ground | 304.44 | m above nearest node |  | Tank Cost | € 1,155,519.79
Tank volume | 804.56 | m3 |  | Total Pipe Replacement Cost | € 731,954.30
|  |  |  | Total Investment Cost | € 2,564,034.42
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P169 | 277.6 | 2068.2 | 400 | 253 | 523254.6
P175 | 277.6 | 764.9 | 400 | 253 | 193519.7
1 | 277.6 | 60 | 400 | 253 | 15180