## Summary
Summary of results for tank connected to each node
| Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
0 | J68 | 3 | 50.66 | 17.57 | 17.59 | € 117.20 | 279.05 | 98.1 | 18.1 | 202.36 | 20.1 | 22 | J68 | [] | € 220,783.94 | € 341,339.23 | € 0.00 | € 562,123.17 | € 7,146.39 | € 49,008.46 | € 98,933.08
1 | pump1 | 0 | 51.89 | 17.57 | 17.59 | € 120.02 | 285.75 | 101.91 | 71.91 | 202.36 | 20.07 | 7 | J68 | [] | € 220,783.94 | € 374,006.26 | € 0.00 | € 594,790.20 | € 7,407.73 | € 51,856.52 | € 103,070.09

## J68
This sheet contains the results for tank connected to node: J68
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.66 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 17.57 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 17.59 | L/s |  | Critical Node | J68
Cost: | € 117.20 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 279.05 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 98.1 | m above sea level |  | Pump Cost | € 220,783.94
Tank height above ground | 18.1 | m above nearest node |  | Tank Cost | € 341,339.23
Tank volume | 202.36 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 562,123.17
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost

## pump1
This sheet contains the results for tank connected to node: pump1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.89 | m |  | Minimum Pressure | 20.07 | mwc
Duty Flow | 17.57 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 17.59 | L/s |  | Critical Node | J68
Cost: | € 120.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 285.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 101.91 | m above sea level |  | Pump Cost | € 220,783.94
Tank height above ground | 71.91 | m above nearest node |  | Tank Cost | € 374,006.26
Tank volume | 202.36 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 594,790.20
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost