## Summary
Summary of results for tank connected to each node

## J1
This sheet contains the results for tank connected to node: J1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 64.44 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.28 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,385.33 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17584.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 131.45 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 111.45 | m above nearest node |  | Tank Cost | € 5,059,184.31
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,704,689.09
|  |  |  | Total Investment Cost | € 13,780,930.54
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 355 | 240 | 215532
P36 | 123.4 | 276.61 | 200 | 79 | 21852.19
P37 | 176.2 | 679.18 | 315 | 190 | 129044.2
P38 | 176.2 | 672.53 | 315 | 190 | 127780.7
P39 | 176.2 | 674.91 | 700 | 590 | 398196.9
P40 | 198.2 | 554.7 | 500 | 348 | 193035.6
P41 | 176.2 | 527.23 | 450 | 295 | 155532.85
P43 | 198.2 | 649.61 | 355 | 240 | 155906.4
P44 | 54.9 | 479.64 | 140 | 41 | 19665.24
P46 | 110.2 | 325.48 | 225 | 100 | 32548
P47 | 54.9 | 573.88 | 200 | 79 | 45336.52
P48 | 220.4 | 449.92 | 315 | 190 | 85484.8
P49 | 176.2 | 910.77 | 315 | 190 | 173046.3
P50 | 198.2 | 191.46 | 315 | 190 | 36377.4
P51 | 54.9 | 454.51 | 160 | 52 | 23634.52
P52 | 220.4 | 425.98 | 450 | 295 | 125664.1
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 315 | 190 | 132188.7
P56 | 277.6 | 665.66 | 450 | 295 | 196369.7
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 500 | 348 | 118243.44
P62 | 54.9 | 493.75 | 125 | 34 | 16787.5
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 125 | 34 | 28325.4
P76 | 220.4 | 390.88 | 315 | 190 | 74267.2
P77 | 54.9 | 541.9 | 160 | 52 | 28178.8
P128 | 54.9 | 343.05 | 200 | 79 | 27100.95
P130 | 176.2 | 813.25 | 450 | 295 | 239908.75
P180 | 141 | 237.74 | 200 | 79 | 18781.46
P181 | 110.2 | 255.04 | 200 | 79 | 20148.16
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J2
This sheet contains the results for tank connected to node: J2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 77.19 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.26 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 8,864.48 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 21105.92 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 155.62 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 135.62 | m above nearest node |  | Tank Cost | € 5,771,690.15
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,161,823.91
|  |  |  | Total Investment Cost | € 12,950,571.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P15 | 277.6 | 967.37 | 700 | 590 | 570748.3
P16 | 54.9 | 961.61 | 160 | 52 | 50003.72
P19 | 54.9 | 979.49 | 140 | 41 | 40159.09
P162 | 450 | 330.04 | 700 | 590 | 194723.6
P213 | 400 | 743.08 | 700 | 590 | 438417.2
P214 | 400 | 1244.68 | 700 | 590 | 734361.2
P215 | 400 | 110.58 | 700 | 590 | 65242.2
3 | 450 | 114.54 | 700 | 590 | 67578.6
26 | 450 | 1 | 700 | 590 | 590

## J3
This sheet contains the results for tank connected to node: J3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 72.54 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 8,336.61 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 19849.07 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 152.31 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 132.31 | m above nearest node |  | Tank Cost | € 5,674,014.65
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,862,149.44
|  |  |  | Total Investment Cost | € 12,553,221.23
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P162 | 450 | 330.04 | 800 | 732 | 241589.28
P213 | 400 | 743.08 | 800 | 732 | 543934.56
P214 | 400 | 1244.68 | 800 | 732 | 911105.76
P215 | 400 | 110.58 | 800 | 732 | 80944.56
3 | 450 | 114.54 | 800 | 732 | 83843.28
26 | 450 | 1 | 800 | 732 | 732

## J4
This sheet contains the results for tank connected to node: J4
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 78.5 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.79 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 9,016.22 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 21467.2 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 156.72 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 126.72 | m above nearest node |  | Tank Cost | € 5,509,180.06
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,356,342.00
|  |  |  | Total Investment Cost | € 12,882,579.20
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P12 | 312.8 | 747.45 | 700 | 590 | 440995.5
P13 | 220.4 | 610.31 | 700 | 590 | 360082.9
P16 | 54.9 | 961.61 | 110 | 28 | 26925.08
P19 | 54.9 | 979.49 | 110 | 28 | 27425.72
P162 | 450 | 330.04 | 700 | 590 | 194723.6
P213 | 400 | 743.08 | 700 | 590 | 438417.2
P214 | 400 | 1244.68 | 700 | 590 | 734361.2
P215 | 400 | 110.58 | 700 | 590 | 65242.2
3 | 450 | 114.54 | 700 | 590 | 67578.6
26 | 450 | 1 | 700 | 590 | 590

## J5
This sheet contains the results for tank connected to node: J5
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 79.15 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 9,088.12 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 21638.38 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 157.24 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 147.24 | m above nearest node |  | Tank Cost | € 6,114,263.09
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,475,061.80
|  |  |  | Total Investment Cost | € 13,606,382.03
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P159 | 312.8 | 161.55 | 700 | 590 | 95314.5
P160 | 312.8 | 935.29 | 700 | 590 | 551821.1
P213 | 400 | 743.08 | 700 | 590 | 438417.2
P214 | 400 | 1244.68 | 700 | 590 | 734361.2
P216 | 277.6 | 952.88 | 700 | 590 | 562199.2
P217 | 277.6 | 156.54 | 700 | 590 | 92358.6
27 | 312.8 | 1 | 700 | 590 | 590

## J6
This sheet contains the results for tank connected to node: J6
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.91 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,212.86 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17173.48 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.55 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.55 | m above nearest node |  | Tank Cost | € 5,327,586.28
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,771,353.59
|  |  |  | Total Investment Cost | € 13,115,997.02
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 110 | 28 | 25145.4
P38 | 176.2 | 672.53 | 250 | 120 | 80703.6
P40 | 198.2 | 554.7 | 400 | 253 | 140339.1
P41 | 176.2 | 527.23 | 500 | 348 | 183476.04
P42 | 66 | 583.01 | 200 | 79 | 46057.79
P43 | 198.2 | 649.61 | 250 | 120 | 77953.2
P44 | 54.9 | 479.64 | 110 | 28 | 13429.92
P46 | 110.2 | 325.48 | 200 | 79 | 25712.92
P47 | 54.9 | 573.88 | 250 | 120 | 68865.6
P48 | 220.4 | 449.92 | 250 | 120 | 53990.4
P49 | 176.2 | 910.77 | 225 | 100 | 91077
P50 | 198.2 | 191.46 | 225 | 100 | 19146
P51 | 54.9 | 454.51 | 125 | 34 | 15453.34
P52 | 220.4 | 425.98 | 355 | 240 | 102235.2
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 500 | 348 | 242114.04
P56 | 277.6 | 665.66 | 500 | 348 | 231649.68
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 500 | 348 | 118243.44
P62 | 54.9 | 493.75 | 200 | 79 | 39006.25
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P65 | 277.6 | 190.09 | 315 | 190 | 36117.1
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 75 | 17 | 14162.7
P76 | 220.4 | 390.88 | 225 | 100 | 39088
P77 | 54.9 | 541.9 | 160 | 52 | 28178.8
P128 | 54.9 | 343.05 | 110 | 28 | 9605.4
P130 | 176.2 | 813.25 | 355 | 240 | 195180
P181 | 110.2 | 255.04 | 125 | 34 | 8671.36
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J7
This sheet contains the results for tank connected to node: J7
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 61.86 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,096.95 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16897.5 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.16 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.16 | m above nearest node |  | Tank Cost | € 5,315,929.81
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,564,834.56
|  |  |  | Total Investment Cost | € 11,897,821.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P36 | 123.4 | 276.61 | 125 | 34 | 9404.74
P42 | 66 | 583.01 | 90 | 21 | 12243.21
P44 | 54.9 | 479.64 | 125 | 34 | 16307.76
P46 | 110.2 | 325.48 | 250 | 120 | 39057.6
P47 | 54.9 | 573.88 | 200 | 79 | 45336.52
P48 | 220.4 | 449.92 | 315 | 190 | 85484.8
P49 | 176.2 | 910.77 | 315 | 190 | 173046.3
P50 | 198.2 | 191.46 | 315 | 190 | 36377.4
P62 | 54.9 | 493.75 | 160 | 52 | 25675
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P65 | 277.6 | 190.09 | 700 | 590 | 112153.1
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 140 | 41 | 34157.1
P76 | 220.4 | 390.88 | 250 | 120 | 46905.6
P77 | 54.9 | 541.9 | 160 | 52 | 28178.8
P128 | 54.9 | 343.05 | 125 | 34 | 11663.7
P194 | 277.6 | 396.71 | 700 | 590 | 234058.9
P195 | 277.6 | 325.92 | 700 | 590 | 192292.8
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J8
This sheet contains the results for tank connected to node: J8
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.24 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,250.81 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17263.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.93 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.93 | m above nearest node |  | Tank Cost | € 5,338,578.63
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,171,947.93
|  |  |  | Total Investment Cost | € 12,527,583.71
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 110 | 28 | 25145.4
P36 | 123.4 | 276.61 | 160 | 52 | 14383.72
P38 | 176.2 | 672.53 | 225 | 100 | 67253
P42 | 66 | 583.01 | 140 | 41 | 23903.41
P44 | 54.9 | 479.64 | 160 | 52 | 24941.28
P46 | 110.2 | 325.48 | 355 | 240 | 78115.2
P47 | 54.9 | 573.88 | 125 | 34 | 19511.92
P48 | 220.4 | 449.92 | 600 | 462 | 207863.04
P49 | 176.2 | 910.77 | 355 | 240 | 218584.8
P50 | 198.2 | 191.46 | 700 | 590 | 112961.4
P60 | 312.8 | 353.67 | 315 | 190 | 67197.3
P61 | 312.8 | 339.78 | 315 | 190 | 64558.2
P62 | 54.9 | 493.75 | 90 | 21 | 10368.75
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P65 | 277.6 | 190.09 | 600 | 462 | 87821.58
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 200 | 79 | 65814.9
P71 | 141 | 629.24 | 200 | 79 | 49709.96
P75 | 54.9 | 423.73 | 90 | 21 | 8898.33
P76 | 220.4 | 390.88 | 315 | 190 | 74267.2
P77 | 54.9 | 541.9 | 225 | 100 | 54190
P78 | 277.6 | 452.88 | 315 | 190 | 86047.2
P128 | 54.9 | 343.05 | 140 | 41 | 14065.05
P194 | 277.6 | 396.71 | 600 | 462 | 183280.02
P195 | 277.6 | 325.92 | 600 | 462 | 150575.04
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J9
This sheet contains the results for tank connected to node: J9
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.4 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.26 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,267.73 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17304.13 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.85 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.85 | m above nearest node |  | Tank Cost | € 5,336,347.42
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,828,502.20
|  |  |  | Total Investment Cost | € 13,181,906.76
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 125 | 34 | 30533.7
P36 | 123.4 | 276.61 | 200 | 79 | 21852.19
P38 | 176.2 | 672.53 | 250 | 120 | 80703.6
P40 | 198.2 | 554.7 | 200 | 79 | 43821.3
P42 | 66 | 583.01 | 200 | 79 | 46057.79
P44 | 54.9 | 479.64 | 225 | 100 | 47964
P45 | 176.2 | 590.92 | 250 | 120 | 70910.4
P46 | 110.2 | 325.48 | 450 | 295 | 96016.6
P47 | 54.9 | 573.88 | 110 | 28 | 16068.64
P48 | 220.4 | 449.92 | 600 | 462 | 207863.04
P49 | 176.2 | 910.77 | 600 | 462 | 420775.74
P50 | 198.2 | 191.46 | 600 | 462 | 88454.52
P51 | 54.9 | 454.51 | 110 | 28 | 12726.28
P54 | 176.2 | 312.86 | 200 | 79 | 24715.94
P55 | 198.2 | 695.73 | 200 | 79 | 54962.67
P59 | 400 | 258.95 | 450 | 295 | 76390.25
P60 | 312.8 | 353.67 | 450 | 295 | 104332.65
P61 | 312.8 | 339.78 | 450 | 295 | 100235.1
P64 | 450 | 379.31 | 600 | 462 | 175241.22
P65 | 277.6 | 190.09 | 600 | 462 | 87821.58
P66 | 400 | 139.14 | 600 | 462 | 64282.68
P68 | 54.9 | 408.47 | 225 | 100 | 40847
P70 | 54.9 | 833.1 | 160 | 52 | 43321.2
P71 | 141 | 629.24 | 160 | 52 | 32720.48
P75 | 54.9 | 423.73 | 63 | 14 | 5932.22
P76 | 220.4 | 390.88 | 450 | 295 | 115309.6
P77 | 54.9 | 541.9 | 125 | 34 | 18424.6
P78 | 277.6 | 452.88 | 450 | 295 | 133599.6
P128 | 54.9 | 343.05 | 200 | 79 | 27100.95
P130 | 176.2 | 813.25 | 225 | 100 | 81325
P194 | 277.6 | 396.71 | 600 | 462 | 183280.02
P195 | 277.6 | 325.92 | 600 | 462 | 150575.04
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J10
This sheet contains the results for tank connected to node: J10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 68.9 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,891.94 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18790.35 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 134.86 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 124.86 | m above nearest node |  | Tank Cost | € 5,454,364.06
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 4,000,964.64
|  |  |  | Total Investment Cost | € 14,472,385.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 315 | 190 | 170629.5
P36 | 123.4 | 276.61 | 600 | 462 | 127793.82
P37 | 176.2 | 679.18 | 600 | 462 | 313781.16
P38 | 176.2 | 672.53 | 400 | 253 | 170150.09
P39 | 176.2 | 674.91 | 315 | 190 | 128232.9
P40 | 198.2 | 554.7 | 315 | 190 | 105393
P42 | 66 | 583.01 | 125 | 34 | 19822.34
P43 | 198.2 | 649.61 | 500 | 348 | 226064.28
P44 | 54.9 | 479.64 | 110 | 28 | 13429.92
P45 | 176.2 | 590.92 | 315 | 190 | 112274.8
P47 | 54.9 | 573.88 | 125 | 34 | 19511.92
P48 | 220.4 | 449.92 | 315 | 190 | 85484.8
P49 | 176.2 | 910.77 | 315 | 190 | 173046.3
P50 | 198.2 | 191.46 | 315 | 190 | 36377.4
P51 | 54.9 | 454.51 | 140 | 41 | 18634.91
P52 | 220.4 | 425.98 | 355 | 240 | 102235.2
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 315 | 190 | 132188.7
P56 | 277.6 | 665.66 | 355 | 240 | 159758.4
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 500 | 348 | 118243.44
P62 | 54.9 | 493.75 | 90 | 21 | 10368.75
P63 | 500 | 342.19 | 600 | 462 | 158091.78
P65 | 277.6 | 190.09 | 355 | 240 | 45621.6
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 140 | 41 | 34157.1
P76 | 220.4 | 390.88 | 500 | 348 | 136026.24
P77 | 54.9 | 541.9 | 160 | 52 | 28178.8
P78 | 277.6 | 452.88 | 500 | 348 | 157602.24
P127 | 176.2 | 662.58 | 315 | 190 | 125890.2
P128 | 54.9 | 343.05 | 315 | 190 | 65179.5
P130 | 176.2 | 813.25 | 355 | 240 | 195180
P181 | 110.2 | 255.04 | 140 | 41 | 10456.64
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P194 | 277.6 | 396.71 | 315 | 190 | 75374.9
P195 | 277.6 | 325.92 | 315 | 190 | 61924.8
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J11
This sheet contains the results for tank connected to node: J11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.64 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,295.58 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17370.43 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 131.02 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 121.02 | m above nearest node |  | Tank Cost | € 5,341,189.92
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,420,978.28
|  |  |  | Total Investment Cost | € 13,779,225.35
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 160 | 52 | 46698.6
P36 | 123.4 | 276.61 | 225 | 100 | 27661
P37 | 176.2 | 679.18 | 200 | 79 | 53655.22
P38 | 176.2 | 672.53 | 250 | 120 | 80703.6
P42 | 66 | 583.01 | 225 | 100 | 58301
P44 | 54.9 | 479.64 | 250 | 120 | 57556.8
P45 | 176.2 | 590.92 | 700 | 590 | 348642.8
P46 | 110.2 | 325.48 | 500 | 348 | 113267.04
P47 | 54.9 | 573.88 | 90 | 21 | 12051.48
P48 | 220.4 | 449.92 | 600 | 462 | 207863.04
P49 | 176.2 | 910.77 | 600 | 462 | 420775.74
P50 | 198.2 | 191.46 | 600 | 462 | 88454.52
P51 | 54.9 | 454.51 | 125 | 34 | 15453.34
P54 | 176.2 | 312.86 | 200 | 79 | 24715.94
P55 | 198.2 | 695.73 | 225 | 100 | 69573
P58 | 450 | 296.06 | 500 | 348 | 103028.88
P59 | 400 | 258.95 | 500 | 348 | 90114.6
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 450 | 295 | 100235.1
P64 | 450 | 379.31 | 600 | 462 | 175241.22
P65 | 277.6 | 190.09 | 600 | 462 | 87821.58
P66 | 400 | 139.14 | 600 | 462 | 64282.68
P68 | 54.9 | 408.47 | 225 | 100 | 40847
P70 | 54.9 | 833.1 | 160 | 52 | 43321.2
P71 | 141 | 629.24 | 160 | 52 | 32720.48
P76 | 220.4 | 390.88 | 450 | 295 | 115309.6
P77 | 54.9 | 541.9 | 125 | 34 | 18424.6
P78 | 277.6 | 452.88 | 450 | 295 | 133599.6
P127 | 176.2 | 662.58 | 225 | 100 | 66258
P128 | 54.9 | 343.05 | 225 | 100 | 34305
P130 | 176.2 | 813.25 | 225 | 100 | 81325
P181 | 110.2 | 255.04 | 125 | 34 | 8671.36
P183 | 198.2 | 238.36 | 200 | 79 | 18830.44
P194 | 277.6 | 396.71 | 600 | 462 | 183280.02
P195 | 277.6 | 325.92 | 600 | 462 | 150575.04
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J12
This sheet contains the results for tank connected to node: J12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 64.23 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,362.36 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17529.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 131.18 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 121.18 | m above nearest node |  | Tank Cost | € 5,346,076.51
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,631,948.77
|  |  |  | Total Investment Cost | € 13,995,082.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 200 | 79 | 70945.95
P36 | 123.4 | 276.61 | 140 | 41 | 11341.01
P37 | 176.2 | 679.18 | 225 | 100 | 67918
P38 | 176.2 | 672.53 | 500 | 348 | 234040.44
P39 | 176.2 | 674.91 | 200 | 79 | 53317.89
P40 | 198.2 | 554.7 | 400 | 253 | 140339.1
P41 | 176.2 | 527.23 | 250 | 120 | 63267.6
P42 | 66 | 583.01 | 140 | 41 | 23903.41
P43 | 198.2 | 649.61 | 600 | 462 | 300119.82
P44 | 54.9 | 479.64 | 200 | 79 | 37891.56
P45 | 176.2 | 590.92 | 225 | 100 | 59092
P46 | 110.2 | 325.48 | 250 | 120 | 39057.6
P47 | 54.9 | 573.88 | 140 | 41 | 23529.08
P48 | 220.4 | 449.92 | 315 | 190 | 85484.8
P49 | 176.2 | 910.77 | 315 | 190 | 173046.3
P50 | 198.2 | 191.46 | 315 | 190 | 36377.4
P51 | 54.9 | 454.51 | 140 | 41 | 18634.91
P52 | 220.4 | 425.98 | 355 | 240 | 102235.2
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 355 | 240 | 166975.2
P56 | 277.6 | 665.66 | 400 | 253 | 168411.98
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 500 | 348 | 118243.44
P62 | 54.9 | 493.75 | 90 | 21 | 10368.75
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P65 | 277.6 | 190.09 | 315 | 190 | 36117.1
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 125 | 34 | 28325.4
P76 | 220.4 | 390.88 | 500 | 348 | 136026.24
P77 | 54.9 | 541.9 | 200 | 79 | 42810.1
P78 | 277.6 | 452.88 | 500 | 348 | 157602.24
P128 | 54.9 | 343.05 | 160 | 52 | 17838.6
P130 | 176.2 | 813.25 | 355 | 240 | 195180
P181 | 110.2 | 255.04 | 140 | 41 | 10456.64
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P194 | 277.6 | 396.71 | 315 | 190 | 75374.9
P195 | 277.6 | 325.92 | 315 | 190 | 61924.8
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J13
This sheet contains the results for tank connected to node: J13
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.94 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,329.05 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17450.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 131.1 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 111.1 | m above nearest node |  | Tank Cost | € 5,048,986.30
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,997,533.02
|  |  |  | Total Investment Cost | € 13,063,576.47
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 160 | 52 | 46698.6
P38 | 176.2 | 672.53 | 400 | 253 | 170150.09
P40 | 198.2 | 554.7 | 500 | 348 | 193035.6
P41 | 176.2 | 527.23 | 450 | 295 | 155532.85
P42 | 66 | 583.01 | 75 | 17 | 9911.17
P43 | 198.2 | 649.61 | 400 | 253 | 164351.33
P44 | 54.9 | 479.64 | 140 | 41 | 19665.24
P46 | 110.2 | 325.48 | 200 | 79 | 25712.92
P47 | 54.9 | 573.88 | 200 | 79 | 45336.52
P48 | 220.4 | 449.92 | 250 | 120 | 53990.4
P49 | 176.2 | 910.77 | 250 | 120 | 109292.4
P50 | 198.2 | 191.46 | 225 | 100 | 19146
P51 | 54.9 | 454.51 | 125 | 34 | 15453.34
P52 | 220.4 | 425.98 | 450 | 295 | 125664.1
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 315 | 190 | 132188.7
P56 | 277.6 | 665.66 | 450 | 295 | 196369.7
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 500 | 348 | 118243.44
P62 | 54.9 | 493.75 | 125 | 34 | 16787.5
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 110 | 28 | 23326.8
P76 | 220.4 | 390.88 | 355 | 240 | 93811.2
P77 | 54.9 | 541.9 | 160 | 52 | 28178.8
P78 | 277.6 | 452.88 | 355 | 240 | 108691.2
P128 | 54.9 | 343.05 | 125 | 34 | 11663.7
P130 | 176.2 | 813.25 | 450 | 295 | 239908.75
P181 | 110.2 | 255.04 | 125 | 34 | 8671.36
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J14
This sheet contains the results for tank connected to node: J14
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.84 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,206.80 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17159.04 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.84 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.84 | m above nearest node |  | Tank Cost | € 5,336,017.94
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,084,085.39
|  |  |  | Total Investment Cost | € 12,437,160.48
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 63 | 14 | 6714.96
P46 | 110.2 | 325.48 | 200 | 79 | 25712.92
P47 | 54.9 | 573.88 | 160 | 52 | 29841.76
P49 | 176.2 | 910.77 | 200 | 79 | 71950.83
P50 | 198.2 | 191.46 | 250 | 120 | 22975.2
P62 | 54.9 | 493.75 | 125 | 34 | 16787.5
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P67 | 277.6 | 401.98 | 700 | 590 | 237168.2
P68 | 54.9 | 408.47 | 225 | 100 | 40847
P69 | 220.4 | 552.65 | 700 | 590 | 326063.5
P70 | 54.9 | 833.1 | 315 | 190 | 158289
P71 | 141 | 629.24 | 700 | 590 | 371251.6
P72 | 198.2 | 365.17 | 700 | 590 | 215450.3
P73 | 54.9 | 417.85 | 140 | 41 | 17131.85
P75 | 54.9 | 423.73 | 200 | 79 | 33474.67
P77 | 54.9 | 541.9 | 200 | 79 | 42810.1
P79 | 110.2 | 382.15 | 200 | 79 | 30189.85
P128 | 54.9 | 343.05 | 90 | 21 | 7204.05
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J15
This sheet contains the results for tank connected to node: J15
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,161.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17050.7 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.6 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.6 | m above nearest node |  | Tank Cost | € 5,328,839.64
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,656,995.34
|  |  |  | Total Investment Cost | € 12,002,892.13
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 63 | 14 | 6714.96
P46 | 110.2 | 325.48 | 160 | 52 | 16924.96
P47 | 54.9 | 573.88 | 125 | 34 | 19511.92
P62 | 54.9 | 493.75 | 90 | 21 | 10368.75
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P67 | 277.6 | 401.98 | 700 | 590 | 237168.2
P68 | 54.9 | 408.47 | 225 | 100 | 40847
P69 | 220.4 | 552.65 | 700 | 590 | 326063.5
P70 | 54.9 | 833.1 | 225 | 100 | 83310
P71 | 141 | 629.24 | 225 | 100 | 62924
P72 | 198.2 | 365.17 | 700 | 590 | 215450.3
P73 | 54.9 | 417.85 | 160 | 52 | 21728.2
P75 | 54.9 | 423.73 | 225 | 100 | 42373
P77 | 54.9 | 541.9 | 125 | 34 | 18424.6
P79 | 110.2 | 382.15 | 225 | 100 | 38215
P128 | 54.9 | 343.05 | 75 | 17 | 5831.85
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P240 | 176.2 | 809.17 | 225 | 100 | 80917

## J16
This sheet contains the results for tank connected to node: J16
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 67.23 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,702.66 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18339.67 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 133.49 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 123.49 | m above nearest node |  | Tank Cost | € 5,414,021.38
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 4,011,255.13
|  |  |  | Total Investment Cost | € 14,442,333.66
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 355 | 240 | 215532
P36 | 123.4 | 276.61 | 225 | 100 | 27661
P37 | 176.2 | 679.18 | 600 | 462 | 313781.16
P38 | 176.2 | 672.53 | 400 | 253 | 170150.09
P39 | 176.2 | 674.91 | 355 | 240 | 161978.4
P40 | 198.2 | 554.7 | 400 | 253 | 140339.1
P41 | 176.2 | 527.23 | 250 | 120 | 63267.6
P42 | 66 | 583.01 | 110 | 28 | 16324.28
P43 | 198.2 | 649.61 | 500 | 348 | 226064.28
P44 | 54.9 | 479.64 | 160 | 52 | 24941.28
P45 | 176.2 | 590.92 | 250 | 120 | 70910.4
P46 | 110.2 | 325.48 | 200 | 79 | 25712.92
P47 | 54.9 | 573.88 | 125 | 34 | 19511.92
P48 | 220.4 | 449.92 | 315 | 190 | 85484.8
P49 | 176.2 | 910.77 | 315 | 190 | 173046.3
P50 | 198.2 | 191.46 | 315 | 190 | 36377.4
P51 | 54.9 | 454.51 | 140 | 41 | 18634.91
P52 | 220.4 | 425.98 | 355 | 240 | 102235.2
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 355 | 240 | 166975.2
P56 | 277.6 | 665.66 | 400 | 253 | 168411.98
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 500 | 348 | 123077.16
P61 | 312.8 | 339.78 | 500 | 348 | 118243.44
P62 | 54.9 | 493.75 | 90 | 21 | 10368.75
P63 | 500 | 342.19 | 600 | 462 | 158091.78
P65 | 277.6 | 190.09 | 315 | 190 | 36117.1
P68 | 54.9 | 408.47 | 160 | 52 | 21240.44
P70 | 54.9 | 833.1 | 125 | 34 | 28325.4
P76 | 220.4 | 390.88 | 500 | 348 | 136026.24
P77 | 54.9 | 541.9 | 200 | 79 | 42810.1
P78 | 277.6 | 452.88 | 500 | 348 | 157602.24
P127 | 176.2 | 662.58 | 225 | 100 | 66258
P128 | 54.9 | 343.05 | 225 | 100 | 34305
P130 | 176.2 | 813.25 | 355 | 240 | 195180
P181 | 110.2 | 255.04 | 140 | 41 | 10456.64
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P194 | 277.6 | 396.71 | 315 | 190 | 75374.9
P195 | 277.6 | 325.92 | 315 | 190 | 61924.8
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J17
This sheet contains the results for tank connected to node: J17
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.19 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.3 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,245.05 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17250.11 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.7 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.7 | m above nearest node |  | Tank Cost | € 5,331,736.55
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,145,397.25
|  |  |  | Total Investment Cost | € 13,494,190.95
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 140 | 41 | 36820.05
P38 | 176.2 | 672.53 | 355 | 240 | 161407.2
P40 | 198.2 | 554.7 | 315 | 190 | 105393
P42 | 66 | 583.01 | 225 | 100 | 58301
P43 | 198.2 | 649.61 | 400 | 253 | 164351.33
P44 | 54.9 | 479.64 | 125 | 34 | 16307.76
P46 | 110.2 | 325.48 | 355 | 240 | 78115.2
P47 | 54.9 | 573.88 | 140 | 41 | 23529.08
P48 | 220.4 | 449.92 | 355 | 240 | 107980.8
P49 | 176.2 | 910.77 | 355 | 240 | 218584.8
P50 | 198.2 | 191.46 | 355 | 240 | 45950.4
P51 | 54.9 | 454.51 | 140 | 41 | 18634.91
P52 | 220.4 | 425.98 | 315 | 190 | 80936.2
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P55 | 198.2 | 695.73 | 315 | 190 | 132188.7
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P60 | 312.8 | 353.67 | 600 | 462 | 163395.54
P61 | 312.8 | 339.78 | 600 | 462 | 156978.36
P62 | 54.9 | 493.75 | 110 | 28 | 13825
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P65 | 277.6 | 190.09 | 355 | 240 | 45621.6
P68 | 54.9 | 408.47 | 160 | 52 | 21240.44
P70 | 54.9 | 833.1 | 110 | 28 | 23326.8
P76 | 220.4 | 390.88 | 600 | 462 | 180586.56
P77 | 54.9 | 541.9 | 140 | 41 | 22217.9
P78 | 277.6 | 452.88 | 600 | 462 | 209230.56
P128 | 54.9 | 343.05 | 125 | 34 | 11663.7
P130 | 176.2 | 813.25 | 315 | 190 | 154517.5
P181 | 110.2 | 255.04 | 140 | 41 | 10456.64
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P194 | 277.6 | 396.71 | 355 | 240 | 95210.4
P195 | 277.6 | 325.92 | 355 | 240 | 78220.8
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J18
This sheet contains the results for tank connected to node: J18
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.17 | m |  | Minimum Pressure | 20.07 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,130.98 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16978.52 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.31 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.31 | m above nearest node |  | Tank Cost | € 5,320,515.94
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,245,480.97
|  |  |  | Total Investment Cost | € 12,583,054.05
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P36 | 123.4 | 276.61 | 140 | 41 | 11341.01
P38 | 176.2 | 672.53 | 225 | 100 | 67253
P42 | 66 | 583.01 | 125 | 34 | 19822.34
P44 | 54.9 | 479.64 | 160 | 52 | 24941.28
P45 | 176.2 | 590.92 | 200 | 79 | 46682.68
P46 | 110.2 | 325.48 | 315 | 190 | 61841.2
P47 | 54.9 | 573.88 | 140 | 41 | 23529.08
P48 | 220.4 | 449.92 | 700 | 590 | 265452.8
P49 | 176.2 | 910.77 | 355 | 240 | 218584.8
P50 | 198.2 | 191.46 | 355 | 240 | 45950.4
P60 | 312.8 | 353.67 | 315 | 190 | 67197.3
P61 | 312.8 | 339.78 | 315 | 190 | 64558.2
P62 | 54.9 | 493.75 | 125 | 34 | 16787.5
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P65 | 277.6 | 190.09 | 700 | 590 | 112153.1
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P68 | 54.9 | 408.47 | 200 | 79 | 32269.13
P70 | 54.9 | 833.1 | 160 | 52 | 43321.2
P71 | 141 | 629.24 | 160 | 52 | 32720.48
P75 | 54.9 | 423.73 | 63 | 14 | 5932.22
P76 | 220.4 | 390.88 | 315 | 190 | 74267.2
P77 | 54.9 | 541.9 | 225 | 100 | 54190
P78 | 277.6 | 452.88 | 315 | 190 | 86047.2
P128 | 54.9 | 343.05 | 140 | 41 | 14065.05
P194 | 277.6 | 396.71 | 700 | 590 | 234058.9
P195 | 277.6 | 325.92 | 700 | 590 | 192292.8
P203 | 450 | 210.74 | 700 | 590 | 124336.6

## J19
This sheet contains the results for tank connected to node: J19
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.04 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,725.48 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13632.09 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 114.76 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 104.76 | m above nearest node |  | Tank Cost | € 4,861,854.64
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,915,206.17
|  |  |  | Total Investment Cost | € 12,794,117.95
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 600 | 462 | 381256.26
P81 | 54.9 | 524.52 | 700 | 590 | 309466.8
P82 | 141 | 365.95 | 700 | 590 | 215910.5
P83 | 54.9 | 453.04 | 315 | 190 | 86077.6
P84 | 176.2 | 621.54 | 315 | 190 | 118092.6
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P89 | 54.9 | 605.09 | 125 | 34 | 20573.06
P92 | 123.4 | 328.23 | 200 | 79 | 25930.17
P93 | 54.9 | 443.19 | 200 | 79 | 35012.01
P94 | 141 | 478.6 | 200 | 79 | 37809.4
P95 | 54.9 | 382.77 | 200 | 79 | 30238.83
P98 | 54.9 | 457.88 | 75 | 17 | 7783.96
P105 | 54.9 | 740.68 | 75 | 17 | 12591.56
P178 | 277.6 | 318.48 | 600 | 462 | 147137.76
P179 | 277.6 | 548.03 | 600 | 462 | 253189.86
P186 | 277.6 | 73.68 | 355 | 240 | 17683.2
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J20
This sheet contains the results for tank connected to node: J20
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 47.83 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,479.45 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13046.32 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 113.87 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 103.87 | m above nearest node |  | Tank Cost | € 4,835,639.61
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,814,001.31
|  |  |  | Total Investment Cost | € 11,666,698.07
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 700 | 590 | 486885.7
P83 | 54.9 | 453.04 | 160 | 52 | 23558.08
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P92 | 123.4 | 328.23 | 160 | 52 | 17067.96
P93 | 54.9 | 443.19 | 160 | 52 | 23045.88
P94 | 141 | 478.6 | 160 | 52 | 24887.2
P95 | 54.9 | 382.77 | 140 | 41 | 15693.57
P98 | 54.9 | 457.88 | 63 | 14 | 6410.32
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J21
This sheet contains the results for tank connected to node: J21
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,610.94 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13359.37 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 114.69 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 104.69 | m above nearest node |  | Tank Cost | € 4,859,828.31
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,289,709.40
|  |  |  | Total Investment Cost | € 12,166,594.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 700 | 590 | 486885.7
P83 | 54.9 | 453.04 | 200 | 79 | 35790.16
P92 | 123.4 | 328.23 | 160 | 52 | 17067.96
P93 | 54.9 | 443.19 | 160 | 52 | 23045.88
P94 | 141 | 478.6 | 200 | 79 | 37809.4
P95 | 54.9 | 382.77 | 160 | 52 | 19904.04
P98 | 54.9 | 457.88 | 75 | 17 | 7783.96
P178 | 277.6 | 318.48 | 700 | 590 | 187903.2
P179 | 277.6 | 548.03 | 700 | 590 | 323337.7
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J22
This sheet contains the results for tank connected to node: J22
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.38 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,651.00 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13454.77 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 114.22 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 104.22 | m above nearest node |  | Tank Cost | € 4,846,183.96
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,781,721.67
|  |  |  | Total Investment Cost | € 12,644,962.78
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 600 | 462 | 381256.26
P82 | 141 | 365.95 | 700 | 590 | 215910.5
P83 | 54.9 | 453.04 | 315 | 190 | 86077.6
P84 | 176.2 | 621.54 | 315 | 190 | 118092.6
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P88 | 141 | 641.1 | 250 | 120 | 76932
P89 | 54.9 | 605.09 | 225 | 100 | 60509
P92 | 123.4 | 328.23 | 200 | 79 | 25930.17
P93 | 54.9 | 443.19 | 200 | 79 | 35012.01
P94 | 141 | 478.6 | 200 | 79 | 37809.4
P95 | 54.9 | 382.77 | 200 | 79 | 30238.83
P98 | 54.9 | 457.88 | 75 | 17 | 7783.96
P104 | 96.8 | 638.28 | 160 | 52 | 33190.56
P105 | 54.9 | 740.68 | 160 | 52 | 38515.36
P178 | 277.6 | 318.48 | 600 | 462 | 147137.76
P179 | 277.6 | 548.03 | 600 | 462 | 253189.86
P186 | 277.6 | 73.68 | 355 | 240 | 17683.2
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J23
This sheet contains the results for tank connected to node: J23
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 61.35 | m |  | Minimum Pressure | 20.07 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.73 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,040.90 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16764.05 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 129.92 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 119.92 | m above nearest node |  | Tank Cost | € 5,308,971.24
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 544,912.75
|  |  |  | Total Investment Cost | € 10,870,941.14
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 75 | 17 | 8153.88
P46 | 110.2 | 325.48 | 160 | 52 | 16924.96
P47 | 54.9 | 573.88 | 90 | 21 | 12051.48
P62 | 54.9 | 493.75 | 110 | 28 | 13825
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P73 | 54.9 | 417.85 | 90 | 21 | 8774.85
P74 | 110.2 | 492.33 | 140 | 41 | 20185.53
P77 | 54.9 | 541.9 | 90 | 21 | 11379.9
P128 | 54.9 | 343.05 | 75 | 17 | 5831.85
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J24
This sheet contains the results for tank connected to node: J24
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.58 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.25 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,176.38 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17086.61 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.53 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 110.53 | m above nearest node |  | Tank Cost | € 5,032,169.99
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,971,831.49
|  |  |  | Total Investment Cost | € 12,021,058.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P35 | 96.8 | 898.05 | 110 | 28 | 25145.4
P38 | 176.2 | 672.53 | 225 | 100 | 67253
P41 | 176.2 | 527.23 | 315 | 190 | 100173.7
P42 | 66 | 583.01 | 125 | 34 | 19822.34
P43 | 198.2 | 649.61 | 225 | 100 | 64961
P44 | 54.9 | 479.64 | 90 | 21 | 10072.44
P46 | 110.2 | 325.48 | 160 | 52 | 16924.96
P47 | 54.9 | 573.88 | 140 | 41 | 23529.08
P51 | 54.9 | 454.51 | 125 | 34 | 15453.34
P52 | 220.4 | 425.98 | 250 | 120 | 51117.6
P54 | 176.2 | 312.86 | 355 | 240 | 75086.4
P55 | 198.2 | 695.73 | 315 | 190 | 132188.7
P56 | 277.6 | 665.66 | 600 | 462 | 307534.92
P57 | 277.6 | 786.46 | 400 | 253 | 198974.38
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P62 | 54.9 | 493.75 | 200 | 79 | 39006.25
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P77 | 54.9 | 541.9 | 140 | 41 | 22217.9
P128 | 54.9 | 343.05 | 110 | 28 | 9605.4
P130 | 176.2 | 813.25 | 250 | 120 | 97590
P181 | 110.2 | 255.04 | 125 | 34 | 8671.36
P182 | 220.4 | 121.21 | 355 | 240 | 29090.4
P183 | 198.2 | 238.36 | 355 | 240 | 57206.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J25
This sheet contains the results for tank connected to node: J25
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 61.84 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,094.83 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16892.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.25 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 100.25 | m above nearest node |  | Tank Cost | € 4,729,110.31
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,202,614.98
|  |  |  | Total Investment Cost | € 10,948,782.44
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P46 | 110.2 | 325.48 | 125 | 34 | 11066.32
P47 | 54.9 | 573.88 | 63 | 14 | 8034.32
P51 | 54.9 | 454.51 | 125 | 34 | 15453.34
P54 | 176.2 | 312.86 | 400 | 253 | 79153.58
P56 | 277.6 | 665.66 | 355 | 240 | 159758.4
P57 | 277.6 | 786.46 | 700 | 590 | 464011.4
P62 | 54.9 | 493.75 | 63 | 14 | 6912.5
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P77 | 54.9 | 541.9 | 63 | 14 | 7586.6
P128 | 54.9 | 343.05 | 90 | 21 | 7204.05
P181 | 110.2 | 255.04 | 125 | 34 | 8671.36
P182 | 220.4 | 121.21 | 400 | 253 | 30666.13
P183 | 198.2 | 238.36 | 400 | 253 | 60305.08
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J26
This sheet contains the results for tank connected to node: J26
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 97.12 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.24 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 11,130.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 26501.52 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 171.55 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 131.55 | m above nearest node |  | Tank Cost | € 5,651,836.09
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,427,416.10
|  |  |  | Total Investment Cost | € 13,096,309.34
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P9 | 110.2 | 593.2 | 600 | 462 | 274058.4
P12 | 312.8 | 747.45 | 600 | 462 | 345321.9
P13 | 220.4 | 610.31 | 600 | 462 | 281963.22
P16 | 54.9 | 961.61 | 90 | 21 | 20193.81
P19 | 54.9 | 979.49 | 90 | 21 | 20569.29
P162 | 450 | 330.04 | 600 | 462 | 152478.48
P184 | 176.2 | 184.39 | 600 | 462 | 85188.18
P185 | 176.2 | 448.63 | 600 | 462 | 207267.06
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
P213 | 400 | 743.08 | 600 | 462 | 343302.96
P214 | 400 | 1244.68 | 600 | 462 | 575042.16
P215 | 400 | 110.58 | 600 | 462 | 51087.96
3 | 450 | 114.54 | 600 | 462 | 52917.48
26 | 450 | 1 | 600 | 462 | 462

## J27
This sheet contains the results for tank connected to node: J27
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 83.34 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.3 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 9,578.03 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 22804.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 168.76 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 128.76 | m above nearest node |  | Tank Cost | € 5,569,513.03
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,326,115.50
|  |  |  | Total Investment Cost | € 12,912,685.68
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P1 | 110.2 | 666.81 | 500 | 348 | 232049.88
P2 | 96.8 | 732.94 | 500 | 348 | 255063.12
P3 | 79.2 | 551.25 | 500 | 348 | 191835
P4 | 54.9 | 589.36 | 500 | 348 | 205097.28
P5 | 54.9 | 107.87 | 700 | 590 | 63643.3
P6 | 176.2 | 837.79 | 700 | 590 | 494296.1
P157 | 312.8 | 227.43 | 800 | 732 | 166478.76
P197 | 176.2 | 187.93 | 800 | 732 | 137564.76
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
P235 | 96.8 | 589.64 | 700 | 590 | 347887.6
P261 | 66 | 306.41 | 700 | 590 | 180781.9
P262 | 96.8 | 56.14 | 700 | 590 | 33122.6
25 | 312.8 | 1 | 800 | 732 | 732

## J28
This sheet contains the results for tank connected to node: J28
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.99 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,337.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17469.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 131.77 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 91.77 | m above nearest node |  | Tank Cost | € 4,479,163.93
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,574,923.02
|  |  |  | Total Investment Cost | € 11,071,144.09
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P10 | 66 | 378.78 | 700 | 590 | 223480.2
P51 | 54.9 | 454.51 | 250 | 120 | 54541.2
P53 | 176.2 | 754.47 | 700 | 590 | 445137.3
P54 | 176.2 | 312.86 | 250 | 120 | 37543.2
P57 | 277.6 | 786.46 | 600 | 462 | 363344.52
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P128 | 54.9 | 343.05 | 63 | 14 | 4802.7
P180 | 141 | 237.74 | 250 | 120 | 28528.8
P181 | 110.2 | 255.04 | 250 | 120 | 30604.8
P182 | 220.4 | 121.21 | 250 | 120 | 14545.2
P183 | 198.2 | 238.36 | 250 | 120 | 28603.2
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J29
This sheet contains the results for tank connected to node: J29
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 61.57 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,064.77 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16820.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.01 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 110.01 | m above nearest node |  | Tank Cost | € 5,016,619.64
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 862,642.89
|  |  |  | Total Investment Cost | € 10,896,319.67
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 75 | 17 | 8153.88
P46 | 110.2 | 325.48 | 160 | 52 | 16924.96
P47 | 54.9 | 573.88 | 110 | 28 | 16068.64
P51 | 54.9 | 454.51 | 90 | 21 | 9544.71
P54 | 176.2 | 312.86 | 250 | 120 | 37543.2
P58 | 450 | 296.06 | 700 | 590 | 174675.4
P59 | 400 | 258.95 | 700 | 590 | 152780.5
P62 | 54.9 | 493.75 | 200 | 79 | 39006.25
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P77 | 54.9 | 541.9 | 110 | 28 | 15173.2
P128 | 54.9 | 343.05 | 75 | 17 | 5831.85
P182 | 220.4 | 121.21 | 250 | 120 | 14545.2
P183 | 198.2 | 238.36 | 250 | 120 | 28603.2
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J30
This sheet contains the results for tank connected to node: J30
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.06 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.3 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,118.71 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16949.32 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.26 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.26 | m above nearest node |  | Tank Cost | € 5,318,806.94
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,359,686.69
|  |  |  | Total Investment Cost | € 12,695,550.77
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P38 | 176.2 | 672.53 | 200 | 79 | 53129.87
P41 | 176.2 | 527.23 | 355 | 240 | 126535.2
P42 | 66 | 583.01 | 125 | 34 | 19822.34
P43 | 198.2 | 649.61 | 225 | 100 | 64961
P44 | 54.9 | 479.64 | 110 | 28 | 13429.92
P46 | 110.2 | 325.48 | 225 | 100 | 32548
P47 | 54.9 | 573.88 | 200 | 79 | 45336.52
P48 | 220.4 | 449.92 | 250 | 120 | 53990.4
P49 | 176.2 | 910.77 | 225 | 100 | 91077
P50 | 198.2 | 191.46 | 225 | 100 | 19146
P51 | 54.9 | 454.51 | 110 | 28 | 12726.28
P52 | 220.4 | 425.98 | 250 | 120 | 51117.6
P54 | 176.2 | 312.86 | 250 | 120 | 37543.2
P55 | 198.2 | 695.73 | 315 | 190 | 132188.7
P56 | 277.6 | 665.66 | 315 | 190 | 126475.4
P58 | 450 | 296.06 | 700 | 590 | 174675.4
P59 | 400 | 258.95 | 700 | 590 | 152780.5
P60 | 312.8 | 353.67 | 700 | 590 | 208665.3
P61 | 312.8 | 339.78 | 700 | 590 | 200470.2
P62 | 54.9 | 493.75 | 160 | 52 | 25675
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P68 | 54.9 | 408.47 | 110 | 28 | 11437.16
P70 | 54.9 | 833.1 | 110 | 28 | 23326.8
P76 | 220.4 | 390.88 | 315 | 190 | 74267.2
P77 | 54.9 | 541.9 | 160 | 52 | 28178.8
P78 | 277.6 | 452.88 | 315 | 190 | 86047.2
P128 | 54.9 | 343.05 | 110 | 28 | 9605.4
P130 | 176.2 | 813.25 | 250 | 120 | 97590
P182 | 220.4 | 121.21 | 250 | 120 | 14545.2
P183 | 198.2 | 238.36 | 250 | 120 | 28603.2
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J31
This sheet contains the results for tank connected to node: J31
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 61.49 | m |  | Minimum Pressure | 20.07 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,054.97 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16797.55 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.02 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 120.02 | m above nearest node |  | Tank Cost | € 5,311,833.30
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 868,763.30
|  |  |  | Total Investment Cost | € 11,197,653.74
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 110 | 28 | 13429.92
P46 | 110.2 | 325.48 | 200 | 79 | 25712.92
P47 | 54.9 | 573.88 | 140 | 41 | 23529.08
P48 | 220.4 | 449.92 | 225 | 100 | 44992
P49 | 176.2 | 910.77 | 225 | 100 | 91077
P50 | 198.2 | 191.46 | 225 | 100 | 19146
P62 | 54.9 | 493.75 | 160 | 52 | 25675
P64 | 450 | 379.31 | 700 | 590 | 223792.9
P65 | 277.6 | 190.09 | 700 | 590 | 112153.1
P66 | 400 | 139.14 | 700 | 590 | 82092.6
P68 | 54.9 | 408.47 | 125 | 34 | 13887.98
P70 | 54.9 | 833.1 | 90 | 21 | 17495.1
P73 | 54.9 | 417.85 | 63 | 14 | 5849.9
P77 | 54.9 | 541.9 | 125 | 34 | 18424.6
P128 | 54.9 | 343.05 | 110 | 28 | 9605.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J32
This sheet contains the results for tank connected to node: J32
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 61.18 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,020.66 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16715.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 129.86 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 109.86 | m above nearest node |  | Tank Cost | € 5,012,394.03
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 390,390.55
|  |  |  | Total Investment Cost | € 10,419,841.72
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 63 | 14 | 6714.96
P46 | 110.2 | 325.48 | 125 | 34 | 11066.32
P47 | 54.9 | 573.88 | 63 | 14 | 8034.32
P62 | 54.9 | 493.75 | 75 | 17 | 8393.75
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P77 | 54.9 | 541.9 | 63 | 14 | 7586.6
P128 | 54.9 | 343.05 | 63 | 14 | 4802.7
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J33
This sheet contains the results for tank connected to node: J33
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 63.38 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,267.70 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17304.06 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 131.28 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 101.28 | m above nearest node |  | Tank Cost | € 4,759,551.85
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,566,332.17
|  |  |  | Total Investment Cost | € 11,342,941.17
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P44 | 54.9 | 479.64 | 63 | 14 | 6714.96
P46 | 110.2 | 325.48 | 125 | 34 | 11066.32
P47 | 54.9 | 573.88 | 63 | 14 | 8034.32
P51 | 54.9 | 454.51 | 250 | 120 | 54541.2
P53 | 176.2 | 754.47 | 700 | 590 | 445137.3
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P56 | 277.6 | 665.66 | 315 | 190 | 126475.4
P57 | 277.6 | 786.46 | 600 | 462 | 363344.52
P62 | 54.9 | 493.75 | 63 | 14 | 6912.5
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P77 | 54.9 | 541.9 | 63 | 14 | 7586.6
P128 | 54.9 | 343.05 | 75 | 17 | 5831.85
P180 | 141 | 237.74 | 250 | 120 | 28528.8
P181 | 110.2 | 255.04 | 250 | 120 | 30604.8
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J34
This sheet contains the results for tank connected to node: J34
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 62.94 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.3 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 7,217.22 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17183.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 130.71 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 110.71 | m above nearest node |  | Tank Cost | € 5,037,490.86
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,420,212.65
|  |  |  | Total Investment Cost | € 12,474,760.65
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P38 | 176.2 | 672.53 | 250 | 120 | 80703.6
P40 | 198.2 | 554.7 | 355 | 240 | 133128
P41 | 176.2 | 527.23 | 315 | 190 | 100173.7
P42 | 66 | 583.01 | 75 | 17 | 9911.17
P43 | 198.2 | 649.61 | 250 | 120 | 77953.2
P44 | 54.9 | 479.64 | 125 | 34 | 16307.76
P46 | 110.2 | 325.48 | 160 | 52 | 16924.96
P47 | 54.9 | 573.88 | 200 | 79 | 45336.52
P49 | 176.2 | 910.77 | 200 | 79 | 71950.83
P51 | 54.9 | 454.51 | 160 | 52 | 23634.52
P52 | 220.4 | 425.98 | 700 | 590 | 251328.2
P54 | 176.2 | 312.86 | 315 | 190 | 59443.4
P56 | 277.6 | 665.66 | 600 | 462 | 307534.92
P57 | 277.6 | 786.46 | 355 | 240 | 188750.4
P58 | 450 | 296.06 | 600 | 462 | 136779.72
P59 | 400 | 258.95 | 600 | 462 | 119634.9
P62 | 54.9 | 493.75 | 225 | 100 | 49375
P63 | 500 | 342.19 | 700 | 590 | 201892.1
P65 | 277.6 | 190.09 | 315 | 190 | 36117.1
P68 | 54.9 | 408.47 | 110 | 28 | 11437.16
P77 | 54.9 | 541.9 | 140 | 41 | 22217.9
P128 | 54.9 | 343.05 | 125 | 34 | 11663.7
P130 | 176.2 | 813.25 | 400 | 253 | 205752.25
P180 | 141 | 237.74 | 200 | 79 | 18781.46
P181 | 110.2 | 255.04 | 160 | 52 | 13262.08
P182 | 220.4 | 121.21 | 315 | 190 | 23029.9
P183 | 198.2 | 238.36 | 315 | 190 | 45288.4
P203 | 450 | 210.74 | 700 | 590 | 124336.6
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2

## J35
This sheet contains the results for tank connected to node: J35
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 82.7 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.31 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 9,505.35 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 22631.78 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 168.17 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 98.17 | m above nearest node |  | Tank Cost | € 4,667,673.09
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,033,773.50
|  |  |  | Total Investment Cost | € 10,718,503.74
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P1 | 110.2 | 666.81 | 700 | 590 | 393417.9
P2 | 96.8 | 732.94 | 225 | 100 | 73294
P3 | 79.2 | 551.25 | 225 | 100 | 55125
P4 | 54.9 | 589.36 | 225 | 100 | 58936
P5 | 54.9 | 107.87 | 225 | 100 | 10787
P6 | 176.2 | 837.79 | 225 | 100 | 83779
P157 | 312.8 | 227.43 | 700 | 590 | 134183.7
P197 | 176.2 | 187.93 | 700 | 590 | 110878.7
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
P235 | 96.8 | 589.64 | 225 | 100 | 58964
P261 | 66 | 306.41 | 225 | 100 | 30641
P262 | 96.8 | 56.14 | 225 | 100 | 5614
25 | 312.8 | 1 | 700 | 590 | 590

## J36
This sheet contains the results for tank connected to node: J36
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 79.86 | m |  | Minimum Pressure | 20.03 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 9,182.56 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 21863.23 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 165.56 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 105.56 | m above nearest node |  | Tank Cost | € 4,885,608.83
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 322,338.72
|  |  |  | Total Investment Cost | € 10,225,004.69
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P157 | 312.8 | 227.43 | 800 | 732 | 166478.76
P197 | 176.2 | 187.93 | 800 | 732 | 137564.76
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
25 | 312.8 | 1 | 800 | 732 | 732

## J37
This sheet contains the results for tank connected to node: J37
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 83.31 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.75 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 9,576.74 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 22801.77 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 168.69 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 118.69 | m above nearest node |  | Tank Cost | € 5,272,563.16
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 944,733.54
|  |  |  | Total Investment Cost | € 11,234,353.84
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P1 | 110.2 | 666.81 | 160 | 52 | 34674.12
P2 | 96.8 | 732.94 | 160 | 52 | 38112.88
P3 | 79.2 | 551.25 | 160 | 52 | 28665
P4 | 54.9 | 589.36 | 160 | 52 | 30646.72
P5 | 54.9 | 107.87 | 160 | 52 | 5609.24
P6 | 176.2 | 837.79 | 700 | 590 | 494296.1
P157 | 312.8 | 227.43 | 700 | 590 | 134183.7
P197 | 176.2 | 187.93 | 700 | 590 | 110878.7
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
P235 | 96.8 | 589.64 | 160 | 52 | 30661.28
P261 | 66 | 306.41 | 160 | 52 | 15933.32
P262 | 96.8 | 56.14 | 160 | 52 | 2919.28
25 | 312.8 | 1 | 700 | 590 | 590

## J39
This sheet contains the results for tank connected to node: J39
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 88.19 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.75 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 10,133.37 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 24127.06 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 173.12 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 113.12 | m above nearest node |  | Tank Cost | € 5,108,535.95
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,627,696.80
|  |  |  | Total Investment Cost | € 11,753,289.90
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P7 | 176.2 | 846.66 | 700 | 590 | 499529.4
P157 | 312.8 | 227.43 | 700 | 590 | 134183.7
P197 | 176.2 | 187.93 | 700 | 590 | 110878.7
P199 | 277.6 | 787.35 | 700 | 590 | 464536.5
P200 | 220.4 | 678.67 | 700 | 590 | 400415.3
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
25 | 312.8 | 1 | 700 | 590 | 590

## J40
This sheet contains the results for tank connected to node: J40
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.99 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.3 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,384.47 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 12820.17 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 113.41 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 103.41 | m above nearest node |  | Tank Cost | € 4,822,056.21
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,255,110.80
|  |  |  | Total Investment Cost | € 11,094,224.16
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P85 | 198.2 | 552.26 | 315 | 190 | 104929.4
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J41
This sheet contains the results for tank connected to node: J41
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 45.55 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,213.61 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 12413.37 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 110.74 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 80.74 | m above nearest node |  | Tank Cost | € 4,154,053.44
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,936,068.85
|  |  |  | Total Investment Cost | € 11,107,179.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 160 | 52 | 23558.08
P85 | 198.2 | 552.26 | 355 | 240 | 132542.4
P92 | 123.4 | 328.23 | 140 | 41 | 13457.43
P93 | 54.9 | 443.19 | 140 | 41 | 18170.79
P95 | 54.9 | 382.77 | 140 | 41 | 15693.57
P186 | 277.6 | 73.68 | 700 | 590 | 43471.2
P187 | 312.8 | 189.68 | 700 | 590 | 111911.2
P188 | 277.6 | 443.36 | 600 | 462 | 204832.32
P189 | 277.6 | 385.65 | 600 | 462 | 178170.3
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 600 | 462 | 33809.16
P207 | 312.8 | 354.87 | 355 | 240 | 85168.8
P257 | 400 | 78.62 | 600 | 462 | 36322.44
P258 | 400 | 170.08 | 600 | 462 | 78576.96
21 | 312.8 | 1 | 355 | 240 | 240
22 | 400 | 1 | 600 | 462 | 462

## J42
This sheet contains the results for tank connected to node: J42
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.55 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,099.01 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 12140.5 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 109.81 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 89.81 | m above nearest node |  | Tank Cost | € 4,421,375.00
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,787,508.70
|  |  |  | Total Investment Cost | € 11,225,940.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 140 | 41 | 18574.64
P85 | 198.2 | 552.26 | 400 | 253 | 139721.78
P92 | 123.4 | 328.23 | 140 | 41 | 13457.43
P93 | 54.9 | 443.19 | 140 | 41 | 18170.79
P95 | 54.9 | 382.77 | 140 | 41 | 15693.57
P188 | 277.6 | 443.36 | 600 | 462 | 204832.32
P189 | 277.6 | 385.65 | 600 | 462 | 178170.3
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 600 | 462 | 33809.16
P207 | 312.8 | 354.87 | 400 | 253 | 89782.11
P257 | 400 | 78.62 | 600 | 462 | 36322.44
P258 | 400 | 170.08 | 600 | 462 | 78576.96
21 | 312.8 | 1 | 400 | 253 | 253
22 | 400 | 1 | 600 | 462 | 462

## J43
This sheet contains the results for tank connected to node: J43
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.5 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.76 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,891.66 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 14027.76 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 115.72 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 105.72 | m above nearest node |  | Tank Cost | € 4,890,423.45
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,064,734.46
|  |  |  | Total Investment Cost | € 12,972,215.05
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 600 | 462 | 381256.26
P82 | 141 | 365.95 | 600 | 462 | 169068.9
P83 | 54.9 | 453.04 | 200 | 79 | 35790.16
P84 | 176.2 | 621.54 | 200 | 79 | 49101.66
P85 | 198.2 | 552.26 | 225 | 100 | 55226
P88 | 141 | 641.1 | 600 | 462 | 296188.2
P89 | 54.9 | 605.09 | 315 | 190 | 114967.1
P91 | 220.4 | 524.84 | 315 | 190 | 99719.6
P92 | 123.4 | 328.23 | 225 | 100 | 32823
P93 | 54.9 | 443.19 | 225 | 100 | 44319
P94 | 141 | 478.6 | 200 | 79 | 37809.4
P95 | 54.9 | 382.77 | 225 | 100 | 38277
P98 | 54.9 | 457.88 | 75 | 17 | 7783.96
P104 | 96.8 | 638.28 | 225 | 100 | 63828
P105 | 54.9 | 740.68 | 225 | 100 | 74068
P178 | 277.6 | 318.48 | 600 | 462 | 147137.76
P179 | 277.6 | 548.03 | 600 | 462 | 253189.86
P186 | 277.6 | 73.68 | 315 | 190 | 13999.2
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J44
This sheet contains the results for tank connected to node: J44
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 48.57 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.3 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,559.87 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13237.77 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 113.93 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 103.93 | m above nearest node |  | Tank Cost | € 4,837,659.65
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,289,562.50
|  |  |  | Total Investment Cost | € 13,144,279.29
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 700 | 590 | 486885.7
P82 | 141 | 365.95 | 200 | 79 | 28910.05
P83 | 54.9 | 453.04 | 200 | 79 | 35790.16
P84 | 176.2 | 621.54 | 200 | 79 | 49101.66
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P87 | 220.4 | 750.03 | 700 | 590 | 442517.7
P88 | 141 | 641.1 | 200 | 79 | 50646.9
P89 | 54.9 | 605.09 | 200 | 79 | 47802.11
P90 | 176.2 | 529.07 | 225 | 100 | 52907
P91 | 220.4 | 524.84 | 315 | 190 | 99719.6
P92 | 123.4 | 328.23 | 225 | 100 | 32823
P93 | 54.9 | 443.19 | 225 | 100 | 44319
P94 | 141 | 478.6 | 200 | 79 | 37809.4
P95 | 54.9 | 382.77 | 225 | 100 | 38277
P98 | 54.9 | 457.88 | 75 | 17 | 7783.96
P104 | 96.8 | 638.28 | 140 | 41 | 26169.48
P105 | 54.9 | 740.68 | 140 | 41 | 30367.88
P178 | 277.6 | 318.48 | 700 | 590 | 187903.2
P179 | 277.6 | 548.03 | 700 | 590 | 323337.7
P186 | 277.6 | 73.68 | 315 | 190 | 13999.2
P187 | 312.8 | 189.68 | 315 | 190 | 36039.2
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J45
This sheet contains the results for tank connected to node: J45
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.49 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.26 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,319.28 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 12664.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 111.32 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 91.32 | m above nearest node |  | Tank Cost | € 4,465,697.70
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 2,579,689.49
|  |  |  | Total Investment Cost | € 12,062,444.34
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 125 | 34 | 15403.36
P85 | 198.2 | 552.26 | 355 | 240 | 132542.4
P86 | 277.6 | 416.78 | 700 | 590 | 245900.2
P89 | 54.9 | 605.09 | 63 | 14 | 8471.26
P91 | 220.4 | 524.84 | 700 | 590 | 309655.6
P92 | 123.4 | 328.23 | 200 | 79 | 25930.17
P93 | 54.9 | 443.19 | 200 | 79 | 35012.01
P94 | 141 | 478.6 | 160 | 52 | 24887.2
P95 | 54.9 | 382.77 | 200 | 79 | 30238.83
P98 | 54.9 | 457.88 | 63 | 14 | 6410.32
P105 | 54.9 | 740.68 | 75 | 17 | 12591.56
P186 | 277.6 | 73.68 | 700 | 590 | 43471.2
P187 | 312.8 | 189.68 | 700 | 590 | 111911.2
P188 | 277.6 | 443.36 | 600 | 462 | 204832.32
P189 | 277.6 | 385.65 | 600 | 462 | 178170.3
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 600 | 462 | 33809.16
P207 | 312.8 | 354.87 | 355 | 240 | 85168.8
P257 | 400 | 78.62 | 600 | 462 | 36322.44
P258 | 400 | 170.08 | 600 | 462 | 78576.96
21 | 312.8 | 1 | 355 | 240 | 240
22 | 400 | 1 | 600 | 462 | 462

## J46
This sheet contains the results for tank connected to node: J46
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.82 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.75 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 5,698.86 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13568.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 113.86 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 103.86 | m above nearest node |  | Tank Cost | € 4,835,451.82
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,400,509.30
|  |  |  | Total Investment Cost | € 13,253,018.27
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 600 | 462 | 381256.26
P82 | 141 | 365.95 | 200 | 79 | 28910.05
P83 | 54.9 | 453.04 | 200 | 79 | 35790.16
P85 | 198.2 | 552.26 | 315 | 190 | 104929.4
P86 | 277.6 | 416.78 | 355 | 240 | 100027.2
P87 | 220.4 | 750.03 | 600 | 462 | 346513.86
P88 | 141 | 641.1 | 200 | 79 | 50646.9
P89 | 54.9 | 605.09 | 90 | 21 | 12706.89
P90 | 176.2 | 529.07 | 600 | 462 | 244430.34
P91 | 220.4 | 524.84 | 355 | 240 | 125961.6
P92 | 123.4 | 328.23 | 200 | 79 | 25930.17
P93 | 54.9 | 443.19 | 200 | 79 | 35012.01
P94 | 141 | 478.6 | 355 | 240 | 114864
P95 | 54.9 | 382.77 | 355 | 240 | 91864.8
P98 | 54.9 | 457.88 | 110 | 28 | 12820.64
P104 | 96.8 | 638.28 | 160 | 52 | 33190.56
P105 | 54.9 | 740.68 | 160 | 52 | 38515.36
P178 | 277.6 | 318.48 | 600 | 462 | 147137.76
P179 | 277.6 | 548.03 | 600 | 462 | 253189.86
P186 | 277.6 | 73.68 | 400 | 253 | 18641.04
P187 | 312.8 | 189.68 | 400 | 253 | 47989.04
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J47
This sheet contains the results for tank connected to node: J47
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.96 | m |  | Minimum Pressure | 19.96 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.79 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 5,944.09 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 14152.61 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 115.9 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 105.9 | m above nearest node |  | Tank Cost | € 4,895,718.45
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,840,639.31
|  |  |  | Total Investment Cost | € 13,753,414.90
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P80 | 312.8 | 825.23 | 600 | 462 | 381256.26
P82 | 141 | 365.95 | 600 | 462 | 169068.9
P83 | 54.9 | 453.04 | 200 | 79 | 35790.16
P84 | 176.2 | 621.54 | 200 | 79 | 49101.66
P85 | 198.2 | 552.26 | 315 | 190 | 104929.4
P86 | 277.6 | 416.78 | 355 | 240 | 100027.2
P87 | 220.4 | 750.03 | 250 | 120 | 90003.6
P88 | 141 | 641.1 | 600 | 462 | 296188.2
P89 | 54.9 | 605.09 | 200 | 79 | 47802.11
P90 | 176.2 | 529.07 | 315 | 190 | 100523.3
P91 | 220.4 | 524.84 | 355 | 240 | 125961.6
P92 | 123.4 | 328.23 | 225 | 100 | 32823
P93 | 54.9 | 443.19 | 225 | 100 | 44319
P94 | 141 | 478.6 | 315 | 190 | 90934
P95 | 54.9 | 382.77 | 315 | 190 | 72726.3
P98 | 54.9 | 457.88 | 110 | 28 | 12820.64
P104 | 96.8 | 638.28 | 600 | 462 | 294885.36
P105 | 54.9 | 740.68 | 355 | 240 | 177763.2
P178 | 277.6 | 318.48 | 600 | 462 | 147137.76
P179 | 277.6 | 548.03 | 600 | 462 | 253189.86
P186 | 277.6 | 73.68 | 355 | 240 | 17683.2
P187 | 312.8 | 189.68 | 355 | 240 | 45523.2
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
22 | 400 | 1 | 700 | 590 | 590

## J48
This sheet contains the results for tank connected to node: J48
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 72.76 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.26 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 8,272.94 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 19697.47 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 122.47 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 112.47 | m above nearest node |  | Tank Cost | € 5,089,149.06
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,598,376.03
|  |  |  | Total Investment Cost | € 11,704,582.24
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P95 | 54.9 | 382.77 | 90 | 21 | 8038.17
P99 | 312.8 | 289.83 | 600 | 462 | 133901.46
P101 | 400 | 349.64 | 600 | 462 | 161533.68
P103 | 277.6 | 1116.12 | 600 | 462 | 515647.44
P106 | 277.6 | 818.42 | 600 | 462 | 378110.04
P152 | 400 | 235.52 | 600 | 462 | 108810.24
P153 | 400 | 211.85 | 600 | 462 | 97874.7
P205 | 312.8 | 73.18 | 355 | 240 | 17563.2
P209 | 277.6 | 238.45 | 600 | 462 | 110163.9
20 | 400 | 1 | 600 | 462 | 462

## J49
This sheet contains the results for tank connected to node: J49
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.46 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.8 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 5,760.99 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 13716.63 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 111.64 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 91.64 | m above nearest node |  | Tank Cost | € 4,475,122.96
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 4,367,152.27
|  |  |  | Total Investment Cost | € 13,859,332.37
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 110 | 28 | 12685.12
P85 | 198.2 | 552.26 | 315 | 190 | 104929.4
P93 | 54.9 | 443.19 | 90 | 21 | 9306.99
P95 | 54.9 | 382.77 | 110 | 28 | 10717.56
P99 | 312.8 | 289.83 | 700 | 590 | 170999.7
P101 | 400 | 349.64 | 700 | 590 | 206287.6
P103 | 277.6 | 1116.12 | 700 | 590 | 658510.8
P152 | 400 | 235.52 | 700 | 590 | 138956.8
P153 | 400 | 211.85 | 700 | 590 | 124991.5
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 315 | 190 | 13904.2
P206 | 600 | 1538.98 | 700 | 590 | 907998.2
P208 | 600 | 1537.13 | 700 | 590 | 906906.7
P209 | 277.6 | 238.45 | 700 | 590 | 140685.5
20 | 400 | 1 | 700 | 590 | 590

## J50
This sheet contains the results for tank connected to node: J50
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 60.56 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.24 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 6,882.55 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16387.01 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 112.04 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 82.04 | m above nearest node |  | Tank Cost | € 4,192,183.79
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 707,302.11
|  |  |  | Total Investment Cost | € 9,916,543.05
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 63 | 14 | 6342.56
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P95 | 54.9 | 382.77 | 90 | 21 | 8038.17
P99 | 312.8 | 289.83 | 600 | 462 | 133901.46
P101 | 400 | 349.64 | 600 | 462 | 161533.68
P152 | 400 | 235.52 | 600 | 462 | 108810.24
P153 | 400 | 211.85 | 600 | 462 | 97874.7
P205 | 312.8 | 73.18 | 315 | 190 | 13904.2
P209 | 277.6 | 238.45 | 600 | 462 | 110163.9
20 | 400 | 1 | 600 | 462 | 462

## J51
This sheet contains the results for tank connected to node: J51
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 45.82 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 8 | hrs
Actual average pumped flow: | 871.29 | L/s |  | Critical Node | R_ALOIK_2
Cost: | € 5,241.94 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 12480.82 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 110.7 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 90.7 | m above nearest node |  | Tank Cost | € 4,447,654.57
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 3,319,759.18
|  |  |  | Total Investment Cost | € 12,784,470.90
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 125 | 34 | 15403.36
P85 | 198.2 | 552.26 | 400 | 253 | 139721.78
P86 | 277.6 | 416.78 | 700 | 590 | 245900.2
P87 | 220.4 | 750.03 | 315 | 190 | 142505.7
P89 | 54.9 | 605.09 | 75 | 17 | 10286.53
P90 | 176.2 | 529.07 | 315 | 190 | 100523.3
P91 | 220.4 | 524.84 | 700 | 590 | 309655.6
P92 | 123.4 | 328.23 | 160 | 52 | 17067.96
P93 | 54.9 | 443.19 | 160 | 52 | 23045.88
P94 | 141 | 478.6 | 700 | 590 | 282374
P95 | 54.9 | 382.77 | 315 | 190 | 72726.3
P96 | 123.4 | 276.37 | 250 | 120 | 33164.4
P97 | 141 | 609.15 | 250 | 120 | 73098
P98 | 54.9 | 457.88 | 250 | 120 | 54945.6
P105 | 54.9 | 740.68 | 110 | 28 | 20739.04
P186 | 277.6 | 73.68 | 700 | 590 | 43471.2
P187 | 312.8 | 189.68 | 700 | 590 | 111911.2
P188 | 277.6 | 443.36 | 600 | 462 | 204832.32
P189 | 277.6 | 385.65 | 600 | 462 | 178170.3
P204 | 600 | 1626.58 | 700 | 590 | 959682.2
P205 | 312.8 | 73.18 | 700 | 590 | 43176.2
P207 | 312.8 | 354.87 | 400 | 253 | 89782.11
P257 | 400 | 78.62 | 700 | 590 | 46385.8
P258 | 400 | 170.08 | 700 | 590 | 100347.2
21 | 312.8 | 1 | 400 | 253 | 253
22 | 400 | 1 | 700 | 590 | 590

## J52
This sheet contains the results for tank connected to node: J52
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 56.93 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.25 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 6,469.95 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 15404.64 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 109.09 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 79.09 | m above nearest node |  | Tank Cost | € 4,105,193.87
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 405,524.41
|  |  |  | Total Investment Cost | € 9,527,775.42
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P95 | 54.9 | 382.77 | 90 | 21 | 8038.17
P152 | 400 | 235.52 | 600 | 462 | 108810.24
P153 | 400 | 211.85 | 600 | 462 | 97874.7
P205 | 312.8 | 73.18 | 315 | 190 | 13904.2
P209 | 277.6 | 238.45 | 600 | 462 | 110163.9
20 | 400 | 1 | 600 | 462 | 462

## J53
This sheet contains the results for tank connected to node: J53
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 65.09 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.25 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 7,380.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17572.45 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 112.85 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 62.85 | m above nearest node |  | Tank Cost | € 3,626,462.88
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,435,523.00
|  |  |  | Total Investment Cost | € 10,079,043.03
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P95 | 54.9 | 382.77 | 63 | 14 | 5358.78
P107 | 54.9 | 757 | 200 | 79 | 59803
P108 | 176.2 | 686.74 | 600 | 462 | 317273.88
P205 | 312.8 | 73.18 | 315 | 190 | 13904.2
P210 | 500 | 2104.87 | 600 | 462 | 972449.94
1 | 500 | 1 | 600 | 462 | 462

## J54
This sheet contains the results for tank connected to node: J54
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 60.66 | m |  | Minimum Pressure | 19.91 | mwc
Duty Flow | 871.51 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 871.51 | L/s |  | Critical Node | R_GOLGOTA
Cost: | € 6,877.68 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16375.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 108.82 | m above sea level |  | Pump Cost | € 5,017,057.15
Tank height above ground | 48.82 | m above nearest node |  | Tank Cost | € 3,213,109.78
Tank volume | 9825.95 | m3 |  | Total Pipe Replacement Cost | € 1,053,563.87
|  |  |  | Total Investment Cost | € 9,283,730.80
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P83 | 54.9 | 453.04 | 63 | 14 | 6342.56
P85 | 198.2 | 552.26 | 250 | 120 | 66271.2
P95 | 54.9 | 382.77 | 90 | 21 | 8038.17
P210 | 500 | 2104.87 | 600 | 462 | 972449.94
1 | 500 | 1 | 600 | 462 | 462