## Summary
Summary of results for tank connected to each node
Column1 | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
0 | 2 | 0 | 51.13 | 269.14 | 269.09 | 1815.32 | 4322.2 | 57.25 | 47.05 | 3824.63 | 19.99 | 17 | 10 | [] | 1959832.98 | 1413533.52 | 0 | 3373366.5 | 55499.18 | 294105.46 | 1012197.97
1 | 3 | 0.51 | 50.61 | 269.14 | 268.05 | 1793.75 | 4270.84 | 56.21 | 39.71 | 3824.63 | 19.99 | 18 | 10 | [] | 1959832.98 | 1329273.47 | 0 | 3289106.45 | 54825.1 | 286759.29 | 996303.79
2 | 4 | 1.44 | 50.56 | 269.14 | 268.1 | 1790.42 | 4262.9 | 55.58 | 32.48 | 3824.63 | 20 | 18 | 10 | [] | 1959832.98 | 1246375.14 | 233160 | 3439368.12 | 54568.71 | 299859.79 | 1007931.69
3 | 5 | 2.41 | 51.46 | 269.14 | 268.08 | 1822.94 | 4340.32 | 56.93 | 38.63 | 3824.63 | 20.04 | 17 | 10 | [] | 1959832.98 | 1316981.35 | 51350 | 3328164.33 | 54983.51 | 290164.53 | 1010519.86
4 | 6 | 1.95 | 50.35 | 269.14 | 268.1 | 1782.75 | 4244.65 | 55.23 | 32.53 | 3824.63 | 20 | 18 | 10 | [] | 1959832.98 | 1246957.45 | 401410 | 3608200.43 | 54971.87 | 314579.36 | 1020256.03
5 | 7 | 2.9 | 49 | 269.14 | 268.12 | 1733.84 | 4128.18 | 53.29 | 23.79 | 3824.63 | 19.99 | 18 | 10 | [] | 1959832.98 | 1146707.9 | 492050 | 3598590.88 | 55591.77 | 313741.55 | 1002183.65
6 | 8 | 3.53 | 51.14 | 269.14 | 268.1 | 1811.01 | 4311.92 | 56.3 | 31.9 | 3824.63 | 20.06 | 17 | 10 | [] | 1959832.98 | 1239712.29 | 249100 | 3448645.27 | 55354.11 | 300668.61 | 1017039.68
7 | 9 | 3.56 | 49.59 | 269.14 | 268.13 | 1755.29 | 4179.26 | 53.92 | 22.22 | 3824.63 | 20 | 18 | 10 | [] | 1959832.98 | 1128646.69 | 413020 | 3501499.67 | 55052.13 | 305276.7 | 1001008.66
8 | 10 | 4.27 | 48.89 | 269.14 | 268.16 | 1728.75 | 4116.08 | 52.68 | 17.98 | 3824.63 | 19.98 | 21 | 10 | [] | 1959832.98 | 1080021.31 | 399600 | 3439454.29 | 54596.03 | 299867.3 | 985458.78
9 | 11 | 12.76 | 51.46 | 269.14 | 268.13 | 1821.45 | 4336.78 | 56.54 | 32.54 | 3824.63 | 20.09 | 17 | 10 | [] | 1959832.98 | 1247018.99 | 370900 | 3577751.97 | 55883.31 | 311924.72 | 1032635.87

## 2
This sheet contains the results for tank connected to node: 2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.13 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 269.09 | L/s |  | Critical Node | 10
Cost: | € 1,815.32 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4322.2 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 57.25 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 47.05 | m above nearest node |  | Tank Cost | € 1,413,533.52
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 3,373,366.50
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost

## 3
This sheet contains the results for tank connected to node: 3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.61 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.05 | L/s |  | Critical Node | 10
Cost: | € 1,793.75 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4270.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.21 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 39.71 | m above nearest node |  | Tank Cost | € 1,329,273.47
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 3,289,106.45
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost

## 4
This sheet contains the results for tank connected to node: 4
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.56 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.1 | L/s |  | Critical Node | 10
Cost: | € 1,790.42 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4262.9 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 55.58 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 32.48 | m above nearest node |  | Tank Cost | € 1,246,375.14
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 233,160.00
|  |  |  | Total Investment Cost | € 3,439,368.12
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
3 | 400 | 600 | 450 | 295 | 177000
10 | 150 | 660 | 160 | 52 | 34320
12 | 150 | 420 | 160 | 52 | 21840

## 5
This sheet contains the results for tank connected to node: 5
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.46 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 268.08 | L/s |  | Critical Node | 10
Cost: | € 1,822.94 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4340.32 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.93 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 38.63 | m above nearest node |  | Tank Cost | € 1,316,981.35
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 51,350.00
|  |  |  | Total Investment Cost | € 3,328,164.33
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
11 | 150 | 650 | 200 | 79 | 51350

## 6
This sheet contains the results for tank connected to node: 6
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.35 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.1 | L/s |  | Critical Node | 10
Cost: | € 1,782.75 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4244.65 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 55.23 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 32.53 | m above nearest node |  | Tank Cost | € 1,246,957.45
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 401,410.00
|  |  |  | Total Investment Cost | € 3,608,200.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
5 | 400 | 950 | 450 | 295 | 280250
10 | 150 | 660 | 160 | 52 | 34320
11 | 150 | 650 | 225 | 100 | 65000
12 | 150 | 420 | 160 | 52 | 21840

## 7
This sheet contains the results for tank connected to node: 7
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.12 | L/s |  | Critical Node | 10
Cost: | € 1,733.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4128.18 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 53.29 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 23.79 | m above nearest node |  | Tank Cost | € 1,146,707.90
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 492,050.00
|  |  |  | Total Investment Cost | € 3,598,590.88
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
6 | 300 | 1050 | 400 | 253 | 265650
9 | 200 | 590 | 225 | 100 | 59000
10 | 150 | 660 | 315 | 190 | 125400
12 | 150 | 420 | 225 | 100 | 42000

## 8
This sheet contains the results for tank connected to node: 8
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.14 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 268.1 | L/s |  | Critical Node | 10
Cost: | € 1,811.01 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4311.92 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.3 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 31.9 | m above nearest node |  | Tank Cost | € 1,239,712.29
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 249,100.00
|  |  |  | Total Investment Cost | € 3,448,645.27
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
7 | 300 | 580 | 450 | 295 | 171100
11 | 150 | 650 | 250 | 120 | 78000

## 9
This sheet contains the results for tank connected to node: 9
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.59 | m |  | Minimum Pressure | 20 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.13 | L/s |  | Critical Node | 10
Cost: | € 1,755.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4179.26 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 53.92 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 22.22 | m above nearest node |  | Tank Cost | € 1,128,646.69
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 413,020.00
|  |  |  | Total Investment Cost | € 3,501,499.67
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
8 | 300 | 780 | 400 | 253 | 197340
9 | 200 | 590 | 225 | 100 | 59000
11 | 150 | 650 | 315 | 190 | 123500
12 | 150 | 420 | 200 | 79 | 33180

## 10
This sheet contains the results for tank connected to node: 10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 48.89 | m |  | Minimum Pressure | 19.98 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 268.16 | L/s |  | Critical Node | 10
Cost: | € 1,728.75 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4116.08 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 52.68 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 17.98 | m above nearest node |  | Tank Cost | € 1,080,021.31
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 399,600.00
|  |  |  | Total Investment Cost | € 3,439,454.29
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
9 | 200 | 590 | 355 | 240 | 141600
10 | 150 | 660 | 250 | 120 | 79200
11 | 150 | 650 | 250 | 120 | 78000
12 | 150 | 420 | 355 | 240 | 100800

## 11
This sheet contains the results for tank connected to node: 11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.46 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 269.14 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 268.13 | L/s |  | Critical Node | 10
Cost: | € 1,821.45 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4336.78 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.54 | m above sea level |  | Pump Cost | € 1,959,832.98
Tank height above ground | 32.54 | m above nearest node |  | Tank Cost | € 1,247,018.99
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | € 370,900.00
|  |  |  | Total Investment Cost | € 3,577,751.97
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
7 | 300 | 580 | 450 | 295 | 171100
11 | 150 | 650 | 250 | 120 | 78000
13 | 200 | 350 | 500 | 348 | 121800