## Summary
Summary of results for tank connected to each node
| Node | Parameter | Value | Units
0 | Summary | for | node: | a01
1 | a01 | Duty Head | 46.57 | m
2 | a01 | Duty Flow | 102.81 | L/s
3 | a01 | Actual average pumped flow: | 102.79 | L/s
4 | a01 | Cost: | €225.43 | Europerday
5 | a01 | Energy: | 1502.89 | kWh/day
6 | a01 | Tank Elevation | 42.62 | m above sea level
7 | a01 | Tank height above ground | 42.62 | m above nearest node
8 | a01 | Tank volume | 1469.6 | m3
9 | a01 | Minimum Pressure | 20.1 | mwc
10 | a01 | Critical Hour | 6 | hrs
11 | a01 | Critical Node | e05 | Node
12 | a01 | Critical Pipes | [] | Unit headloss >10m/km
13 | a01 | Pump Cost | €907,505.33 | Capital Investment
14 | a01 | Tank Cost | €708,340.50 | Capital Investment
15 | a01 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
16 | a01 | Total Investment Cost | €2,141,879.83 | Grand Total
17 | --- | --- | --- | ---
18 | Summary | for | node: | a02
19 | a02 | Duty Head | 44.58 | m
20 | a02 | Duty Flow | 102.81 | L/s
21 | a02 | Actual average pumped flow: | 102.78 | L/s
22 | a02 | Cost: | €215.78 | Europerday
23 | a02 | Energy: | 1438.55 | kWh/day
24 | a02 | Tank Elevation | 39.57 | m above sea level
25 | a02 | Tank height above ground | 39.57 | m above nearest node
26 | a02 | Tank volume | 1469.6 | m3
27 | a02 | Minimum Pressure | 20.09 | mwc
28 | a02 | Critical Hour | 6 | hrs
29 | a02 | Critical Node | e05 | Node
30 | a02 | Critical Pipes | [] | Unit headloss >10m/km
31 | a02 | Pump Cost | €907,505.33 | Capital Investment
32 | a02 | Tank Cost | €694,890.21 | Capital Investment
33 | a02 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
34 | a02 | Total Investment Cost | €2,128,429.53 | Grand Total
35 | --- | --- | --- | ---
36 | Summary | for | node: | a03
37 | a03 | Duty Head | 44.17 | m
38 | a03 | Duty Flow | 102.81 | L/s
39 | a03 | Actual average pumped flow: | 102.74 | L/s
40 | a03 | Cost: | €213.81 | Europerday
41 | a03 | Energy: | 1425.39 | kWh/day
42 | a03 | Tank Elevation | 39.02 | m above sea level
43 | a03 | Tank height above ground | 39.02 | m above nearest node
44 | a03 | Tank volume | 1469.6 | m3
45 | a03 | Minimum Pressure | 20.09 | mwc
46 | a03 | Critical Hour | 6 | hrs
47 | a03 | Critical Node | e05 | Node
48 | a03 | Critical Pipes | [] | Unit headloss >10m/km
49 | a03 | Pump Cost | €907,505.33 | Capital Investment
50 | a03 | Tank Cost | €692,488.29 | Capital Investment
51 | a03 | Total Pipe Replacement Cost | €701,174.00 | Capital Investment
52 | a03 | Total Investment Cost | €2,301,167.61 | Grand Total
53 | --- | --- | --- | ---
54 | Summary | for | node: | a04
55 | a04 | Duty Head | 43.58 | m
56 | a04 | Duty Flow | 102.81 | L/s
57 | a04 | Actual average pumped flow: | 102.78 | L/s
58 | a04 | Cost: | €210.96 | Europerday
59 | a04 | Energy: | 1406.39 | kWh/day
60 | a04 | Tank Elevation | 38.04 | m above sea level
61 | a04 | Tank height above ground | 38.04 | m above nearest node
62 | a04 | Tank volume | 1469.6 | m3
63 | a04 | Minimum Pressure | 20.09 | mwc
64 | a04 | Critical Hour | 6 | hrs
65 | a04 | Critical Node | e05 | Node
66 | a04 | Critical Pipes | [] | Unit headloss >10m/km
67 | a04 | Pump Cost | €907,505.33 | Capital Investment
68 | a04 | Tank Cost | €688,136.32 | Capital Investment
69 | a04 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
70 | a04 | Total Investment Cost | €2,121,675.65 | Grand Total
71 | --- | --- | --- | ---
72 | Summary | for | node: | a05
73 | a05 | Duty Head | 43.62 | m
74 | a05 | Duty Flow | 102.81 | L/s
75 | a05 | Actual average pumped flow: | 102.75 | L/s
76 | a05 | Cost: | €211.17 | Europerday
77 | a05 | Energy: | 1407.77 | kWh/day
78 | a05 | Tank Elevation | 38.21 | m above sea level
79 | a05 | Tank height above ground | 38.21 | m above nearest node
80 | a05 | Tank volume | 1469.6 | m3
81 | a05 | Minimum Pressure | 20.09 | mwc
82 | a05 | Critical Hour | 6 | hrs
83 | a05 | Critical Node | e05 | Node
84 | a05 | Critical Pipes | [] | Unit headloss >10m/km
85 | a05 | Pump Cost | €907,505.33 | Capital Investment
86 | a05 | Tank Cost | €688,891.78 | Capital Investment
87 | a05 | Total Pipe Replacement Cost | €695,279.00 | Capital Investment
88 | a05 | Total Investment Cost | €2,291,676.11 | Grand Total
89 | --- | --- | --- | ---
90 | Summary | for | node: | a06
91 | a06 | Duty Head | 43.12 | m
92 | a06 | Duty Flow | 102.81 | L/s
93 | a06 | Actual average pumped flow: | 102.78 | L/s
94 | a06 | Cost: | €208.71 | Europerday
95 | a06 | Energy: | 1391.42 | kWh/day
96 | a06 | Tank Elevation | 37.33 | m above sea level
97 | a06 | Tank height above ground | 37.33 | m above nearest node
98 | a06 | Tank volume | 1469.6 | m3
99 | a06 | Minimum Pressure | 20.09 | mwc
100 | a06 | Critical Hour | 6 | hrs
101 | a06 | Critical Node | e05 | Node
102 | a06 | Critical Pipes | [] | Unit headloss >10m/km
103 | a06 | Pump Cost | €907,505.33 | Capital Investment
104 | a06 | Tank Cost | €685,018.03 | Capital Investment
105 | a06 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
106 | a06 | Total Investment Cost | €2,118,557.36 | Grand Total
107 | --- | --- | --- | ---
108 | Summary | for | node: | a07
109 | a07 | Duty Head | 42.82 | m
110 | a07 | Duty Flow | 102.81 | L/s
111 | a07 | Actual average pumped flow: | 102.78 | L/s
112 | a07 | Cost: | €207.26 | Europerday
113 | a07 | Energy: | 1381.75 | kWh/day
114 | a07 | Tank Elevation | 36.87 | m above sea level
115 | a07 | Tank height above ground | 36.87 | m above nearest node
116 | a07 | Tank volume | 1469.6 | m3
117 | a07 | Minimum Pressure | 20.09 | mwc
118 | a07 | Critical Hour | 6 | hrs
119 | a07 | Critical Node | e05 | Node
120 | a07 | Critical Pipes | [] | Unit headloss >10m/km
121 | a07 | Pump Cost | €907,505.33 | Capital Investment
122 | a07 | Tank Cost | €682,991.43 | Capital Investment
123 | a07 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
124 | a07 | Total Investment Cost | €2,116,530.76 | Grand Total
125 | --- | --- | --- | ---
126 | Summary | for | node: | a08
127 | a08 | Duty Head | 42.74 | m
128 | a08 | Duty Flow | 102.81 | L/s
129 | a08 | Actual average pumped flow: | 102.76 | L/s
130 | a08 | Cost: | €206.89 | Europerday
131 | a08 | Energy: | 1379.28 | kWh/day
132 | a08 | Tank Elevation | 36.77 | m above sea level
133 | a08 | Tank height above ground | 36.77 | m above nearest node
134 | a08 | Tank volume | 1469.6 | m3
135 | a08 | Minimum Pressure | 20.09 | mwc
136 | a08 | Critical Hour | 6 | hrs
137 | a08 | Critical Node | e05 | Node
138 | a08 | Critical Pipes | [] | Unit headloss >10m/km
139 | a08 | Pump Cost | €907,505.33 | Capital Investment
140 | a08 | Tank Cost | €682,568.77 | Capital Investment
141 | a08 | Total Pipe Replacement Cost | €790,869.00 | Capital Investment
142 | a08 | Total Investment Cost | €2,380,943.10 | Grand Total
143 | --- | --- | --- | ---
144 | Summary | for | node: | a09
145 | a09 | Duty Head | 43 | m
146 | a09 | Duty Flow | 102.81 | L/s
147 | a09 | Actual average pumped flow: | 102.77 | L/s
148 | a09 | Cost: | €208.03 | Europerday
149 | a09 | Energy: | 1386.87 | kWh/day
150 | a09 | Tank Elevation | 36.87 | m above sea level
151 | a09 | Tank height above ground | 36.87 | m above nearest node
152 | a09 | Tank volume | 1469.6 | m3
153 | a09 | Minimum Pressure | 20.1 | mwc
154 | a09 | Critical Hour | 6 | hrs
155 | a09 | Critical Node | e05 | Node
156 | a09 | Critical Pipes | [] | Unit headloss >10m/km
157 | a09 | Pump Cost | €907,505.33 | Capital Investment
158 | a09 | Tank Cost | €682,981.52 | Capital Investment
159 | a09 | Total Pipe Replacement Cost | €833,700.00 | Capital Investment
160 | a09 | Total Investment Cost | €2,424,186.85 | Grand Total
161 | --- | --- | --- | ---
162 | Summary | for | node: | a10
163 | a10 | Duty Head | 42.8 | m
164 | a10 | Duty Flow | 102.81 | L/s
165 | a10 | Actual average pumped flow: | 102.8 | L/s
166 | a10 | Cost: | €207.06 | Europerday
167 | a10 | Energy: | 1380.41 | kWh/day
168 | a10 | Tank Elevation | 36.76 | m above sea level
169 | a10 | Tank height above ground | 36.76 | m above nearest node
170 | a10 | Tank volume | 1469.6 | m3
171 | a10 | Minimum Pressure | 20.1 | mwc
172 | a10 | Critical Hour | 6 | hrs
173 | a10 | Critical Node | e05 | Node
174 | a10 | Critical Pipes | [] | Unit headloss >10m/km
175 | a10 | Pump Cost | €907,505.33 | Capital Investment
176 | a10 | Tank Cost | €682,504.44 | Capital Investment
177 | a10 | Total Pipe Replacement Cost | €890,584.00 | Capital Investment
178 | a10 | Total Investment Cost | €2,480,593.77 | Grand Total
179 | --- | --- | --- | ---
180 | Summary | for | node: | a11
181 | a11 | Duty Head | 43.6 | m
182 | a11 | Duty Flow | 102.81 | L/s
183 | a11 | Actual average pumped flow: | 102.73 | L/s
184 | a11 | Cost: | €210.96 | Europerday
185 | a11 | Energy: | 1406.39 | kWh/day
186 | a11 | Tank Elevation | 37.5 | m above sea level
187 | a11 | Tank height above ground | 37.5 | m above nearest node
188 | a11 | Tank volume | 1469.6 | m3
189 | a11 | Minimum Pressure | 20.1 | mwc
190 | a11 | Critical Hour | 6 | hrs
191 | a11 | Critical Node | e05 | Node
192 | a11 | Critical Pipes | [] | Unit headloss >10m/km
193 | a11 | Pump Cost | €907,505.33 | Capital Investment
194 | a11 | Tank Cost | €685,759.83 | Capital Investment
195 | a11 | Total Pipe Replacement Cost | €901,659.00 | Capital Investment
196 | a11 | Total Investment Cost | €2,494,924.16 | Grand Total
197 | --- | --- | --- | ---
198 | Summary | for | node: | a12
199 | a12 | Duty Head | 43.96 | m
200 | a12 | Duty Flow | 102.81 | L/s
201 | a12 | Actual average pumped flow: | 102.74 | L/s
202 | a12 | Cost: | €212.71 | Europerday
203 | a12 | Energy: | 1418.09 | kWh/day
204 | a12 | Tank Elevation | 37.94 | m above sea level
205 | a12 | Tank height above ground | 37.94 | m above nearest node
206 | a12 | Tank volume | 1469.6 | m3
207 | a12 | Minimum Pressure | 20.09 | mwc
208 | a12 | Critical Hour | 6 | hrs
209 | a12 | Critical Node | e05 | Node
210 | a12 | Critical Pipes | [] | Unit headloss >10m/km
211 | a12 | Pump Cost | €907,505.33 | Capital Investment
212 | a12 | Tank Cost | €687,727.54 | Capital Investment
213 | a12 | Total Pipe Replacement Cost | €942,969.00 | Capital Investment
214 | a12 | Total Investment Cost | €2,538,201.87 | Grand Total
215 | --- | --- | --- | ---
216 | Summary | for | node: | a13
217 | a13 | Duty Head | 44.2 | m
218 | a13 | Duty Flow | 102.81 | L/s
219 | a13 | Actual average pumped flow: | 102.81 | L/s
220 | a13 | Cost: | €213.77 | Europerday
221 | a13 | Energy: | 1425.13 | kWh/day
222 | a13 | Tank Elevation | 38.12 | m above sea level
223 | a13 | Tank height above ground | 38.12 | m above nearest node
224 | a13 | Tank volume | 1469.6 | m3
225 | a13 | Minimum Pressure | 20.01 | mwc
226 | a13 | Critical Hour | 6 | hrs
227 | a13 | Critical Node | e05 | Node
228 | a13 | Critical Pipes | [] | Unit headloss >10m/km
229 | a13 | Pump Cost | €907,505.33 | Capital Investment
230 | a13 | Tank Cost | €688,490.89 | Capital Investment
231 | a13 | Total Pipe Replacement Cost | €1,002,279.00 | Capital Investment
232 | a13 | Total Investment Cost | €2,598,275.21 | Grand Total
233 | --- | --- | --- | ---
234 | Summary | for | node: | a14
235 | a14 | Duty Head | 41.99 | m
236 | a14 | Duty Flow | 102.81 | L/s
237 | a14 | Actual average pumped flow: | 102.81 | L/s
238 | a14 | Cost: | €203.27 | Europerday
239 | a14 | Energy: | 1355.12 | kWh/day
240 | a14 | Tank Elevation | 35.6 | m above sea level
241 | a14 | Tank height above ground | 35.6 | m above nearest node
242 | a14 | Tank volume | 1469.6 | m3
243 | a14 | Minimum Pressure | 20.04 | mwc
244 | a14 | Critical Hour | 6 | hrs
245 | a14 | Critical Node | e05 | Node
246 | a14 | Critical Pipes | [] | Unit headloss >10m/km
247 | a14 | Pump Cost | €907,505.33 | Capital Investment
248 | a14 | Tank Cost | €677,414.25 | Capital Investment
249 | a14 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
250 | a14 | Total Investment Cost | €2,110,953.58 | Grand Total
251 | --- | --- | --- | ---
252 | Summary | for | node: | a15
253 | a15 | Duty Head | 42.78 | m
254 | a15 | Duty Flow | 102.81 | L/s
255 | a15 | Actual average pumped flow: | 102.73 | L/s
256 | a15 | Cost: | €207.06 | Europerday
257 | a15 | Energy: | 1380.4 | kWh/day
258 | a15 | Tank Elevation | 36.55 | m above sea level
259 | a15 | Tank height above ground | 36.55 | m above nearest node
260 | a15 | Tank volume | 1469.6 | m3
261 | a15 | Minimum Pressure | 20.09 | mwc
262 | a15 | Critical Hour | 6 | hrs
263 | a15 | Critical Node | e05 | Node
264 | a15 | Critical Pipes | [] | Unit headloss >10m/km
265 | a15 | Pump Cost | €907,505.33 | Capital Investment
266 | a15 | Tank Cost | €681,594.94 | Capital Investment
267 | a15 | Total Pipe Replacement Cost | €813,504.00 | Capital Investment
268 | a15 | Total Investment Cost | €2,402,604.27 | Grand Total
269 | --- | --- | --- | ---
270 | Summary | for | node: | a16
271 | a16 | Duty Head | 41.79 | m
272 | a16 | Duty Flow | 102.81 | L/s
273 | a16 | Actual average pumped flow: | 102.78 | L/s
274 | a16 | Cost: | €202.26 | Europerday
275 | a16 | Energy: | 1348.42 | kWh/day
276 | a16 | Tank Elevation | 35.27 | m above sea level
277 | a16 | Tank height above ground | 35.27 | m above nearest node
278 | a16 | Tank volume | 1469.6 | m3
279 | a16 | Minimum Pressure | 20.09 | mwc
280 | a16 | Critical Hour | 6 | hrs
281 | a16 | Critical Node | e05 | Node
282 | a16 | Critical Pipes | [] | Unit headloss >10m/km
283 | a16 | Pump Cost | €907,505.33 | Capital Investment
284 | a16 | Tank Cost | €675,938.21 | Capital Investment
285 | a16 | Total Pipe Replacement Cost | €526,034.00 | Capital Investment
286 | a16 | Total Investment Cost | €2,109,477.54 | Grand Total
287 | --- | --- | --- | ---
288 | Summary | for | node: | a17
289 | a17 | Duty Head | 41.09 | m
290 | a17 | Duty Flow | 102.81 | L/s
291 | a17 | Actual average pumped flow: | 102.75 | L/s
292 | a17 | Cost: | €198.90 | Europerday
293 | a17 | Energy: | 1325.99 | kWh/day
294 | a17 | Tank Elevation | 34.5 | m above sea level
295 | a17 | Tank height above ground | 34.5 | m above nearest node
296 | a17 | Tank volume | 1469.6 | m3
297 | a17 | Minimum Pressure | 20.09 | mwc
298 | a17 | Critical Hour | 6 | hrs
299 | a17 | Critical Node | e05 | Node
300 | a17 | Critical Pipes | [] | Unit headloss >10m/km
301 | a17 | Pump Cost | €907,505.33 | Capital Investment
302 | a17 | Tank Cost | €672,548.31 | Capital Investment
303 | a17 | Total Pipe Replacement Cost | €695,444.00 | Capital Investment
304 | a17 | Total Investment Cost | €2,275,497.63 | Grand Total
305 | --- | --- | --- | ---
306 | Summary | for | node: | a18
307 | a18 | Duty Head | 41.73 | m
308 | a18 | Duty Flow | 102.81 | L/s
309 | a18 | Actual average pumped flow: | 102.81 | L/s
310 | a18 | Cost: | €201.85 | Europerday
311 | a18 | Energy: | 1345.67 | kWh/day
312 | a18 | Tank Elevation | 35 | m above sea level
313 | a18 | Tank height above ground | 35 | m above nearest node
314 | a18 | Tank volume | 1469.6 | m3
315 | a18 | Minimum Pressure | 20.08 | mwc
316 | a18 | Critical Hour | 6 | hrs
317 | a18 | Critical Node | e05 | Node
318 | a18 | Critical Pipes | [] | Unit headloss >10m/km
319 | a18 | Pump Cost | €907,505.33 | Capital Investment
320 | a18 | Tank Cost | €674,742.30 | Capital Investment
321 | a18 | Total Pipe Replacement Cost | €730,754.00 | Capital Investment
322 | a18 | Total Investment Cost | €2,313,001.63 | Grand Total
323 | --- | --- | --- | ---
324 | Summary | for | node: | a19
325 | a19 | Duty Head | 39.54 | m
326 | a19 | Duty Flow | 102.81 | L/s
327 | a19 | Actual average pumped flow: | 102.78 | L/s
328 | a19 | Cost: | €191.32 | Europerday
329 | a19 | Energy: | 1275.49 | kWh/day
330 | a19 | Tank Elevation | 32.75 | m above sea level
331 | a19 | Tank height above ground | 32.75 | m above nearest node
332 | a19 | Tank volume | 1469.6 | m3
333 | a19 | Minimum Pressure | 20.1 | mwc
334 | a19 | Critical Hour | 16 | hrs
335 | a19 | Critical Node | e05 | Node
336 | a19 | Critical Pipes | [] | Unit headloss >10m/km
337 | a19 | Pump Cost | €907,505.33 | Capital Investment
338 | a19 | Tank Cost | €664,811.36 | Capital Investment
339 | a19 | Total Pipe Replacement Cost | €628,994.00 | Capital Investment
340 | a19 | Total Investment Cost | €2,201,310.69 | Grand Total
341 | --- | --- | --- | ---
342 | Summary | for | node: | a20
343 | a20 | Duty Head | 39.76 | m
344 | a20 | Duty Flow | 102.81 | L/s
345 | a20 | Actual average pumped flow: | 102.77 | L/s
346 | a20 | Cost: | €192.40 | Europerday
347 | a20 | Energy: | 1282.69 | kWh/day
348 | a20 | Tank Elevation | 33.08 | m above sea level
349 | a20 | Tank height above ground | 33.08 | m above nearest node
350 | a20 | Tank volume | 1469.6 | m3
351 | a20 | Minimum Pressure | 20.09 | mwc
352 | a20 | Critical Hour | 16 | hrs
353 | a20 | Critical Node | e05 | Node
354 | a20 | Critical Pipes | [] | Unit headloss >10m/km
355 | a20 | Pump Cost | €907,505.33 | Capital Investment
356 | a20 | Tank Cost | €666,282.10 | Capital Investment
357 | a20 | Total Pipe Replacement Cost | €823,739.00 | Capital Investment
358 | a20 | Total Investment Cost | €2,397,526.43 | Grand Total
359 | --- | --- | --- | ---
360 | Summary | for | node: | a21
361 | a21 | Duty Head | 40.09 | m
362 | a21 | Duty Flow | 102.81 | L/s
363 | a21 | Actual average pumped flow: | 102.74 | L/s
364 | a21 | Cost: | €194.02 | Europerday
365 | a21 | Energy: | 1293.46 | kWh/day
366 | a21 | Tank Elevation | 33.43 | m above sea level
367 | a21 | Tank height above ground | 33.43 | m above nearest node
368 | a21 | Tank volume | 1469.6 | m3
369 | a21 | Minimum Pressure | 20.09 | mwc
370 | a21 | Critical Hour | 6 | hrs
371 | a21 | Critical Node | e05 | Node
372 | a21 | Critical Pipes | [] | Unit headloss >10m/km
373 | a21 | Pump Cost | €907,505.33 | Capital Investment
374 | a21 | Tank Cost | €667,817.26 | Capital Investment
375 | a21 | Total Pipe Replacement Cost | €892,709.00 | Capital Investment
376 | a21 | Total Investment Cost | €2,468,031.59 | Grand Total
377 | --- | --- | --- | ---
378 | Summary | for | node: | b01
379 | b01 | Duty Head | 37.16 | m
380 | b01 | Duty Flow | 102.81 | L/s
381 | b01 | Actual average pumped flow: | 102.75 | L/s
382 | b01 | Cost: | €179.83 | Europerday
383 | b01 | Energy: | 1198.84 | kWh/day
384 | b01 | Tank Elevation | 30.1 | m above sea level
385 | b01 | Tank height above ground | 30.1 | m above nearest node
386 | b01 | Tank volume | 1469.6 | m3
387 | b01 | Minimum Pressure | 20.09 | mwc
388 | b01 | Critical Hour | 16 | hrs
389 | b01 | Critical Node | e05 | Node
390 | b01 | Critical Pipes | [] | Unit headloss >10m/km
391 | b01 | Pump Cost | €907,505.33 | Capital Investment
392 | b01 | Tank Cost | €653,165.04 | Capital Investment
393 | b01 | Total Pipe Replacement Cost | €762,914.00 | Capital Investment
394 | b01 | Total Investment Cost | €2,323,584.37 | Grand Total
395 | --- | --- | --- | ---
396 | Summary | for | node: | b02
397 | b02 | Duty Head | 37.29 | m
398 | b02 | Duty Flow | 102.81 | L/s
399 | b02 | Actual average pumped flow: | 102.72 | L/s
400 | b02 | Cost: | €180.42 | Europerday
401 | b02 | Energy: | 1202.83 | kWh/day
402 | b02 | Tank Elevation | 30.17 | m above sea level
403 | b02 | Tank height above ground | 30.17 | m above nearest node
404 | b02 | Tank volume | 1469.6 | m3
405 | b02 | Minimum Pressure | 20.1 | mwc
406 | b02 | Critical Hour | 16 | hrs
407 | b02 | Critical Node | e05 | Node
408 | b02 | Critical Pipes | [] | Unit headloss >10m/km
409 | b02 | Pump Cost | €907,505.33 | Capital Investment
410 | b02 | Tank Cost | €653,460.44 | Capital Investment
411 | b02 | Total Pipe Replacement Cost | €901,514.00 | Capital Investment
412 | b02 | Total Investment Cost | €2,462,479.77 | Grand Total
413 | --- | --- | --- | ---
414 | Summary | for | node: | b03
415 | b03 | Duty Head | 37.41 | m
416 | b03 | Duty Flow | 102.81 | L/s
417 | b03 | Actual average pumped flow: | 102.81 | L/s
418 | b03 | Cost: | €180.97 | Europerday
419 | b03 | Energy: | 1206.44 | kWh/day
420 | b03 | Tank Elevation | 30.17 | m above sea level
421 | b03 | Tank height above ground | 30.17 | m above nearest node
422 | b03 | Tank volume | 1469.6 | m3
423 | b03 | Minimum Pressure | 20.09 | mwc
424 | b03 | Critical Hour | 16 | hrs
425 | b03 | Critical Node | e05 | Node
426 | b03 | Critical Pipes | [] | Unit headloss >10m/km
427 | b03 | Pump Cost | €907,505.33 | Capital Investment
428 | b03 | Tank Cost | €653,475.24 | Capital Investment
429 | b03 | Total Pipe Replacement Cost | €990,794.00 | Capital Investment
430 | b03 | Total Investment Cost | €2,551,774.57 | Grand Total
431 | --- | --- | --- | ---
432 | Summary | for | node: | b04
433 | b04 | Duty Head | 37.55 | m
434 | b04 | Duty Flow | 102.81 | L/s
435 | b04 | Actual average pumped flow: | 102.76 | L/s
436 | b04 | Cost: | €181.61 | Europerday
437 | b04 | Energy: | 1210.74 | kWh/day
438 | b04 | Tank Elevation | 30.31 | m above sea level
439 | b04 | Tank height above ground | 30.31 | m above nearest node
440 | b04 | Tank volume | 1469.6 | m3
441 | b04 | Minimum Pressure | 20.1 | mwc
442 | b04 | Critical Hour | 16 | hrs
443 | b04 | Critical Node | e05 | Node
444 | b04 | Critical Pipes | [] | Unit headloss >10m/km
445 | b04 | Pump Cost | €907,505.33 | Capital Investment
446 | b04 | Tank Cost | €654,079.77 | Capital Investment
447 | b04 | Total Pipe Replacement Cost | €1,123,368.00 | Capital Investment
448 | b04 | Total Investment Cost | €2,684,953.10 | Grand Total
449 | --- | --- | --- | ---
450 | Summary | for | node: | b05
451 | b05 | Duty Head | 38.37 | m
452 | b05 | Duty Flow | 102.81 | L/s
453 | b05 | Actual average pumped flow: | 102.81 | L/s
454 | b05 | Cost: | €185.41 | Europerday
455 | b05 | Energy: | 1236.1 | kWh/day
456 | b05 | Tank Elevation | 30.92 | m above sea level
457 | b05 | Tank height above ground | 30.92 | m above nearest node
458 | b05 | Tank volume | 1469.6 | m3
459 | b05 | Minimum Pressure | 19.95 | mwc
460 | b05 | Critical Hour | 16 | hrs
461 | b05 | Critical Node | e05 | Node
462 | b05 | Critical Pipes | [] | Unit headloss >10m/km
463 | b05 | Pump Cost | €907,505.33 | Capital Investment
464 | b05 | Tank Cost | €656,758.23 | Capital Investment
465 | b05 | Total Pipe Replacement Cost | €1,230,660.00 | Capital Investment
466 | b05 | Total Investment Cost | €2,794,923.56 | Grand Total
467 | --- | --- | --- | ---
468 | Summary | for | node: | b06
469 | b06 | Duty Head | 37.62 | m
470 | b06 | Duty Flow | 102.81 | L/s
471 | b06 | Actual average pumped flow: | 102.78 | L/s
472 | b06 | Cost: | €181.93 | Europerday
473 | b06 | Energy: | 1212.84 | kWh/day
474 | b06 | Tank Elevation | 30.36 | m above sea level
475 | b06 | Tank height above ground | 30.36 | m above nearest node
476 | b06 | Tank volume | 1469.6 | m3
477 | b06 | Minimum Pressure | 20.1 | mwc
478 | b06 | Critical Hour | 16 | hrs
479 | b06 | Critical Node | e05 | Node
480 | b06 | Critical Pipes | [] | Unit headloss >10m/km
481 | b06 | Pump Cost | €907,505.33 | Capital Investment
482 | b06 | Tank Cost | €654,282.57 | Capital Investment
483 | b06 | Total Pipe Replacement Cost | €1,175,820.00 | Capital Investment
484 | b06 | Total Investment Cost | €2,737,607.89 | Grand Total
485 | --- | --- | --- | ---
486 | Summary | for | node: | b07
487 | b07 | Duty Head | 38.34 | m
488 | b07 | Duty Flow | 102.81 | L/s
489 | b07 | Actual average pumped flow: | 102.81 | L/s
490 | b07 | Cost: | €185.29 | Europerday
491 | b07 | Energy: | 1235.26 | kWh/day
492 | b07 | Tank Elevation | 30.94 | m above sea level
493 | b07 | Tank height above ground | 30.94 | m above nearest node
494 | b07 | Tank volume | 1469.6 | m3
495 | b07 | Minimum Pressure | 19.99 | mwc
496 | b07 | Critical Hour | 16 | hrs
497 | b07 | Critical Node | e05 | Node
498 | b07 | Critical Pipes | [] | Unit headloss >10m/km
499 | b07 | Pump Cost | €907,505.33 | Capital Investment
500 | b07 | Tank Cost | €656,852.15 | Capital Investment
501 | b07 | Total Pipe Replacement Cost | €1,195,773.00 | Capital Investment
502 | b07 | Total Investment Cost | €2,760,130.47 | Grand Total
503 | --- | --- | --- | ---
504 | Summary | for | node: | b08
505 | b08 | Duty Head | 38.67 | m
506 | b08 | Duty Flow | 102.81 | L/s
507 | b08 | Actual average pumped flow: | 102.74 | L/s
508 | b08 | Cost: | €186.82 | Europerday
509 | b08 | Energy: | 1245.47 | kWh/day
510 | b08 | Tank Elevation | 31.25 | m above sea level
511 | b08 | Tank height above ground | 31.25 | m above nearest node
512 | b08 | Tank volume | 1469.6 | m3
513 | b08 | Minimum Pressure | 20.1 | mwc
514 | b08 | Critical Hour | 16 | hrs
515 | b08 | Critical Node | e05 | Node
516 | b08 | Critical Pipes | [] | Unit headloss >10m/km
517 | b08 | Pump Cost | €907,505.33 | Capital Investment
518 | b08 | Tank Cost | €658,217.49 | Capital Investment
519 | b08 | Total Pipe Replacement Cost | €1,321,665.00 | Capital Investment
520 | b08 | Total Investment Cost | €2,887,387.82 | Grand Total
521 | --- | --- | --- | ---
522 | Summary | for | node: | b09
523 | b09 | Duty Head | 37.59 | m
524 | b09 | Duty Flow | 102.81 | L/s
525 | b09 | Actual average pumped flow: | 102.78 | L/s
526 | b09 | Cost: | €181.79 | Europerday
527 | b09 | Energy: | 1211.95 | kWh/day
528 | b09 | Tank Elevation | 30.34 | m above sea level
529 | b09 | Tank height above ground | 30.34 | m above nearest node
530 | b09 | Tank volume | 1469.6 | m3
531 | b09 | Minimum Pressure | 20.1 | mwc
532 | b09 | Critical Hour | 16 | hrs
533 | b09 | Critical Node | e05 | Node
534 | b09 | Critical Pipes | [] | Unit headloss >10m/km
535 | b09 | Pump Cost | €907,505.33 | Capital Investment
536 | b09 | Tank Cost | €654,219.18 | Capital Investment
537 | b09 | Total Pipe Replacement Cost | €1,175,778.00 | Capital Investment
538 | b09 | Total Investment Cost | €2,737,502.51 | Grand Total
539 | --- | --- | --- | ---
540 | Summary | for | node: | b10
541 | b10 | Duty Head | 38.34 | m
542 | b10 | Duty Flow | 102.81 | L/s
543 | b10 | Actual average pumped flow: | 102.81 | L/s
544 | b10 | Cost: | €185.29 | Europerday
545 | b10 | Energy: | 1235.28 | kWh/day
546 | b10 | Tank Elevation | 31 | m above sea level
547 | b10 | Tank height above ground | 31 | m above nearest node
548 | b10 | Tank volume | 1469.6 | m3
549 | b10 | Minimum Pressure | 19.99 | mwc
550 | b10 | Critical Hour | 16 | hrs
551 | b10 | Critical Node | e05 | Node
552 | b10 | Critical Pipes | [] | Unit headloss >10m/km
553 | b10 | Pump Cost | €907,505.33 | Capital Investment
554 | b10 | Tank Cost | €657,119.84 | Capital Investment
555 | b10 | Total Pipe Replacement Cost | €1,180,008.00 | Capital Investment
556 | b10 | Total Investment Cost | €2,744,633.17 | Grand Total
557 | --- | --- | --- | ---
558 | Summary | for | node: | b11
559 | b11 | Duty Head | 40.13 | m
560 | b11 | Duty Flow | 102.81 | L/s
561 | b11 | Actual average pumped flow: | 102.84 | L/s
562 | b11 | Cost: | €193.64 | Europerday
563 | b11 | Energy: | 1290.91 | kWh/day
564 | b11 | Tank Elevation | 32.17 | m above sea level
565 | b11 | Tank height above ground | 32.17 | m above nearest node
566 | b11 | Tank volume | 1469.6 | m3
567 | b11 | Minimum Pressure | 20.09 | mwc
568 | b11 | Critical Hour | 6 | hrs
569 | b11 | Critical Node | e05 | Node
570 | b11 | Critical Pipes | [] | Unit headloss >10m/km
571 | b11 | Pump Cost | €907,505.33 | Capital Investment
572 | b11 | Tank Cost | €662,259.66 | Capital Investment
573 | b11 | Total Pipe Replacement Cost | €1,231,931.00 | Capital Investment
574 | b11 | Total Investment Cost | €2,801,695.99 | Grand Total
575 | --- | --- | --- | ---
576 | Summary | for | node: | b12
577 | b12 | Duty Head | 38.68 | m
578 | b12 | Duty Flow | 102.81 | L/s
579 | b12 | Actual average pumped flow: | 102.78 | L/s
580 | b12 | Cost: | €186.88 | Europerday
581 | b12 | Energy: | 1245.86 | kWh/day
582 | b12 | Tank Elevation | 31.21 | m above sea level
583 | b12 | Tank height above ground | 31.21 | m above nearest node
584 | b12 | Tank volume | 1469.6 | m3
585 | b12 | Minimum Pressure | 20.1 | mwc
586 | b12 | Critical Hour | 16 | hrs
587 | b12 | Critical Node | e05 | Node
588 | b12 | Critical Pipes | [] | Unit headloss >10m/km
589 | b12 | Pump Cost | €907,505.33 | Capital Investment
590 | b12 | Tank Cost | €658,026.79 | Capital Investment
591 | b12 | Total Pipe Replacement Cost | €1,415,572.00 | Capital Investment
592 | b12 | Total Investment Cost | €2,981,104.11 | Grand Total
593 | --- | --- | --- | ---
594 | Summary | for | node: | c01
595 | c01 | Duty Head | 34 | m
596 | c01 | Duty Flow | 102.81 | L/s
597 | c01 | Actual average pumped flow: | 102.78 | L/s
598 | c01 | Cost: | €164.41 | Europerday
599 | c01 | Energy: | 1096.04 | kWh/day
600 | c01 | Tank Elevation | 26.57 | m above sea level
601 | c01 | Tank height above ground | 26.57 | m above nearest node
602 | c01 | Tank volume | 1469.6 | m3
603 | c01 | Minimum Pressure | 20.1 | mwc
604 | c01 | Critical Hour | 16 | hrs
605 | c01 | Critical Node | b12 | Node
606 | c01 | Critical Pipes | [] | Unit headloss >10m/km
607 | c01 | Pump Cost | €907,505.33 | Capital Investment
608 | c01 | Tank Cost | €637,571.18 | Capital Investment
609 | c01 | Total Pipe Replacement Cost | €1,049,974.00 | Capital Investment
610 | c01 | Total Investment Cost | €2,595,050.51 | Grand Total
611 | --- | --- | --- | ---
612 | Summary | for | node: | c02
613 | c02 | Duty Head | 34.09 | m
614 | c02 | Duty Flow | 102.81 | L/s
615 | c02 | Actual average pumped flow: | 102.77 | L/s
616 | c02 | Cost: | €164.84 | Europerday
617 | c02 | Energy: | 1098.95 | kWh/day
618 | c02 | Tank Elevation | 26.65 | m above sea level
619 | c02 | Tank height above ground | 26.65 | m above nearest node
620 | c02 | Tank volume | 1469.6 | m3
621 | c02 | Minimum Pressure | 20.1 | mwc
622 | c02 | Critical Hour | 16 | hrs
623 | c02 | Critical Node | b12 | Node
624 | c02 | Critical Pipes | [] | Unit headloss >10m/km
625 | c02 | Pump Cost | €907,505.33 | Capital Investment
626 | c02 | Tank Cost | €637,940.03 | Capital Investment
627 | c02 | Total Pipe Replacement Cost | €1,198,284.00 | Capital Investment
628 | c02 | Total Investment Cost | €2,743,729.36 | Grand Total
629 | --- | --- | --- | ---
630 | Summary | for | node: | c03
631 | c03 | Duty Head | 34.74 | m
632 | c03 | Duty Flow | 102.81 | L/s
633 | c03 | Actual average pumped flow: | 102.81 | L/s
634 | c03 | Cost: | €167.85 | Europerday
635 | c03 | Energy: | 1119.03 | kWh/day
636 | c03 | Tank Elevation | 27.16 | m above sea level
637 | c03 | Tank height above ground | 27.16 | m above nearest node
638 | c03 | Tank volume | 1469.6 | m3
639 | c03 | Minimum Pressure | 20.01 | mwc
640 | c03 | Critical Hour | 16 | hrs
641 | c03 | Critical Node | b12 | Node
642 | c03 | Critical Pipes | [] | Unit headloss >10m/km
643 | c03 | Pump Cost | €907,505.33 | Capital Investment
644 | c03 | Tank Cost | €640,173.89 | Capital Investment
645 | c03 | Total Pipe Replacement Cost | €1,269,619.00 | Capital Investment
646 | c03 | Total Investment Cost | €2,817,298.21 | Grand Total
647 | --- | --- | --- | ---
648 | Summary | for | node: | c04
649 | c04 | Duty Head | 34.91 | m
650 | c04 | Duty Flow | 102.81 | L/s
651 | c04 | Actual average pumped flow: | 102.78 | L/s
652 | c04 | Cost: | €168.69 | Europerday
653 | c04 | Energy: | 1124.6 | kWh/day
654 | c04 | Tank Elevation | 27.33 | m above sea level
655 | c04 | Tank height above ground | 27.33 | m above nearest node
656 | c04 | Tank volume | 1469.6 | m3
657 | c04 | Minimum Pressure | 20.1 | mwc
658 | c04 | Critical Hour | 16 | hrs
659 | c04 | Critical Node | b12 | Node
660 | c04 | Critical Pipes | [] | Unit headloss >10m/km
661 | c04 | Pump Cost | €907,505.33 | Capital Investment
662 | c04 | Tank Cost | €640,915.06 | Capital Investment
663 | c04 | Total Pipe Replacement Cost | €1,332,844.00 | Capital Investment
664 | c04 | Total Investment Cost | €2,881,264.38 | Grand Total
665 | --- | --- | --- | ---
666 | Summary | for | node: | c05
667 | c05 | Duty Head | 34.22 | m
668 | c05 | Duty Flow | 102.81 | L/s
669 | c05 | Actual average pumped flow: | 102.78 | L/s
670 | c05 | Cost: | €165.43 | Europerday
671 | c05 | Energy: | 1102.86 | kWh/day
672 | c05 | Tank Elevation | 26.67 | m above sea level
673 | c05 | Tank height above ground | 26.67 | m above nearest node
674 | c05 | Tank volume | 1469.6 | m3
675 | c05 | Minimum Pressure | 20.1 | mwc
676 | c05 | Critical Hour | 16 | hrs
677 | c05 | Critical Node | b12 | Node
678 | c05 | Critical Pipes | [] | Unit headloss >10m/km
679 | c05 | Pump Cost | €907,505.33 | Capital Investment
680 | c05 | Tank Cost | €638,022.14 | Capital Investment
681 | c05 | Total Pipe Replacement Cost | €1,296,246.00 | Capital Investment
682 | c05 | Total Investment Cost | €2,841,773.47 | Grand Total
683 | --- | --- | --- | ---
684 | Summary | for | node: | c06
685 | c06 | Duty Head | 35 | m
686 | c06 | Duty Flow | 102.81 | L/s
687 | c06 | Actual average pumped flow: | 102.81 | L/s
688 | c06 | Cost: | €169.03 | Europerday
689 | c06 | Energy: | 1126.89 | kWh/day
690 | c06 | Tank Elevation | 27.11 | m above sea level
691 | c06 | Tank height above ground | 27.11 | m above nearest node
692 | c06 | Tank volume | 1469.6 | m3
693 | c06 | Minimum Pressure | 19.99 | mwc
694 | c06 | Critical Hour | 16 | hrs
695 | c06 | Critical Node | b12 | Node
696 | c06 | Critical Pipes | [] | Unit headloss >10m/km
697 | c06 | Pump Cost | €907,505.33 | Capital Investment
698 | c06 | Tank Cost | €639,955.10 | Capital Investment
699 | c06 | Total Pipe Replacement Cost | €1,317,184.00 | Capital Investment
700 | c06 | Total Investment Cost | €2,864,644.43 | Grand Total
701 | --- | --- | --- | ---
702 | Summary | for | node: | c07
703 | c07 | Duty Head | 35.38 | m
704 | c07 | Duty Flow | 102.81 | L/s
705 | c07 | Actual average pumped flow: | 102.77 | L/s
706 | c07 | Cost: | €170.84 | Europerday
707 | c07 | Energy: | 1138.92 | kWh/day
708 | c07 | Tank Elevation | 27.56 | m above sea level
709 | c07 | Tank height above ground | 27.56 | m above nearest node
710 | c07 | Tank volume | 1469.6 | m3
711 | c07 | Minimum Pressure | 20.1 | mwc
712 | c07 | Critical Hour | 16 | hrs
713 | c07 | Critical Node | b12 | Node
714 | c07 | Critical Pipes | [] | Unit headloss >10m/km
715 | c07 | Pump Cost | €907,505.33 | Capital Investment
716 | c07 | Tank Cost | €641,962.19 | Capital Investment
717 | c07 | Total Pipe Replacement Cost | €1,336,354.00 | Capital Investment
718 | c07 | Total Investment Cost | €2,885,821.52 | Grand Total
719 | --- | --- | --- | ---
720 | Summary | for | node: | d01
721 | d01 | Duty Head | 34.22 | m
722 | d01 | Duty Flow | 102.81 | L/s
723 | d01 | Actual average pumped flow: | 102.78 | L/s
724 | d01 | Cost: | €165.46 | Europerday
725 | d01 | Energy: | 1103.05 | kWh/day
726 | d01 | Tank Elevation | 26.75 | m above sea level
727 | d01 | Tank height above ground | 26.75 | m above nearest node
728 | d01 | Tank volume | 1469.6 | m3
729 | d01 | Minimum Pressure | 20.1 | mwc
730 | d01 | Critical Hour | 16 | hrs
731 | d01 | Critical Node | b12 | Node
732 | d01 | Critical Pipes | [] | Unit headloss >10m/km
733 | d01 | Pump Cost | €907,505.33 | Capital Investment
734 | d01 | Tank Cost | €638,392.26 | Capital Investment
735 | d01 | Total Pipe Replacement Cost | €1,229,074.00 | Capital Investment
736 | d01 | Total Investment Cost | €2,774,971.58 | Grand Total
737 | --- | --- | --- | ---
738 | Summary | for | node: | d02
739 | d02 | Duty Head | 35.79 | m
740 | d02 | Duty Flow | 102.81 | L/s
741 | d02 | Actual average pumped flow: | 102.84 | L/s
742 | d02 | Cost: | €172.84 | Europerday
743 | d02 | Energy: | 1152.27 | kWh/day
744 | d02 | Tank Elevation | 28.15 | m above sea level
745 | d02 | Tank height above ground | 28.15 | m above nearest node
746 | d02 | Tank volume | 1469.6 | m3
747 | d02 | Minimum Pressure | 20.09 | mwc
748 | d02 | Critical Hour | 6 | hrs
749 | d02 | Critical Node | b12 | Node
750 | d02 | Critical Pipes | [] | Unit headloss >10m/km
751 | d02 | Pump Cost | €907,505.33 | Capital Investment
752 | d02 | Tank Cost | €644,542.28 | Capital Investment
753 | d02 | Total Pipe Replacement Cost | €1,226,014.00 | Capital Investment
754 | d02 | Total Investment Cost | €2,778,061.61 | Grand Total
755 | --- | --- | --- | ---
756 | Summary | for | node: | d03
757 | d03 | Duty Head | 34.34 | m
758 | d03 | Duty Flow | 102.81 | L/s
759 | d03 | Actual average pumped flow: | 102.79 | L/s
760 | d03 | Cost: | €166.02 | Europerday
761 | d03 | Energy: | 1106.78 | kWh/day
762 | d03 | Tank Elevation | 26.86 | m above sea level
763 | d03 | Tank height above ground | 26.86 | m above nearest node
764 | d03 | Tank volume | 1469.6 | m3
765 | d03 | Minimum Pressure | 20.1 | mwc
766 | d03 | Critical Hour | 16 | hrs
767 | d03 | Critical Node | b12 | Node
768 | d03 | Critical Pipes | [] | Unit headloss >10m/km
769 | d03 | Pump Cost | €907,505.33 | Capital Investment
770 | d03 | Tank Cost | €638,849.57 | Capital Investment
771 | d03 | Total Pipe Replacement Cost | €1,322,224.00 | Capital Investment
772 | d03 | Total Investment Cost | €2,868,578.90 | Grand Total
773 | --- | --- | --- | ---
774 | Summary | for | node: | d04
775 | d04 | Duty Head | 42 | m
776 | d04 | Duty Flow | 102.81 | L/s
777 | d04 | Actual average pumped flow: | 102.87 | L/s
778 | d04 | Cost: | €202.09 | Europerday
779 | d04 | Energy: | 1347.27 | kWh/day
780 | d04 | Tank Elevation | 31.06 | m above sea level
781 | d04 | Tank height above ground | 31.06 | m above nearest node
782 | d04 | Tank volume | 1469.6 | m3
783 | d04 | Minimum Pressure | 19.99 | mwc
784 | d04 | Critical Hour | 6 | hrs
785 | d04 | Critical Node | b12 | Node
786 | d04 | Critical Pipes | [] | Unit headloss >10m/km
787 | d04 | Pump Cost | €907,505.33 | Capital Investment
788 | d04 | Tank Cost | €657,371.28 | Capital Investment
789 | d04 | Total Pipe Replacement Cost | €1,150,864.00 | Capital Investment
790 | d04 | Total Investment Cost | €2,715,740.60 | Grand Total
791 | --- | --- | --- | ---
792 | Summary | for | node: | d05
793 | d05 | Duty Head | 34.43 | m
794 | d05 | Duty Flow | 102.81 | L/s
795 | d05 | Actual average pumped flow: | 102.78 | L/s
796 | d05 | Cost: | €166.43 | Europerday
797 | d05 | Energy: | 1109.53 | kWh/day
798 | d05 | Tank Elevation | 26.94 | m above sea level
799 | d05 | Tank height above ground | 26.94 | m above nearest node
800 | d05 | Tank volume | 1469.6 | m3
801 | d05 | Minimum Pressure | 20.1 | mwc
802 | d05 | Critical Hour | 16 | hrs
803 | d05 | Critical Node | b12 | Node
804 | d05 | Critical Pipes | [] | Unit headloss >10m/km
805 | d05 | Pump Cost | €907,505.33 | Capital Investment
806 | d05 | Tank Cost | €639,206.90 | Capital Investment
807 | d05 | Total Pipe Replacement Cost | €1,438,864.00 | Capital Investment
808 | d05 | Total Investment Cost | €2,985,576.23 | Grand Total
809 | --- | --- | --- | ---
810 | Summary | for | node: | d06
811 | d06 | Duty Head | 36.41 | m
812 | d06 | Duty Flow | 102.81 | L/s
813 | d06 | Actual average pumped flow: | 102.84 | L/s
814 | d06 | Cost: | €175.77 | Europerday
815 | d06 | Energy: | 1171.81 | kWh/day
816 | d06 | Tank Elevation | 28.66 | m above sea level
817 | d06 | Tank height above ground | 28.66 | m above nearest node
818 | d06 | Tank volume | 1469.6 | m3
819 | d06 | Minimum Pressure | 20.09 | mwc
820 | d06 | Critical Hour | 6 | hrs
821 | d06 | Critical Node | b12 | Node
822 | d06 | Critical Pipes | [] | Unit headloss >10m/km
823 | d06 | Pump Cost | €907,505.33 | Capital Investment
824 | d06 | Tank Cost | €646,798.73 | Capital Investment
825 | d06 | Total Pipe Replacement Cost | €1,414,214.00 | Capital Investment
826 | d06 | Total Investment Cost | €2,968,518.06 | Grand Total
827 | --- | --- | --- | ---
828 | Summary | for | node: | d07
829 | d07 | Duty Head | 37.03 | m
830 | d07 | Duty Flow | 102.81 | L/s
831 | d07 | Actual average pumped flow: | 102.75 | L/s
832 | d07 | Cost: | €178.64 | Europerday
833 | d07 | Energy: | 1190.94 | kWh/day
834 | d07 | Tank Elevation | 29.32 | m above sea level
835 | d07 | Tank height above ground | 29.32 | m above nearest node
836 | d07 | Tank volume | 1469.6 | m3
837 | d07 | Minimum Pressure | 20.1 | mwc
838 | d07 | Critical Hour | 6 | hrs
839 | d07 | Critical Node | b12 | Node
840 | d07 | Critical Pipes | [] | Unit headloss >10m/km
841 | d07 | Pump Cost | €907,505.33 | Capital Investment
842 | d07 | Tank Cost | €649,715.93 | Capital Investment
843 | d07 | Total Pipe Replacement Cost | €1,490,434.00 | Capital Investment
844 | d07 | Total Investment Cost | €3,047,655.26 | Grand Total
845 | --- | --- | --- | ---
846 | Summary | for | node: | d08
847 | d08 | Duty Head | 37.53 | m
848 | d08 | Duty Flow | 102.81 | L/s
849 | d08 | Actual average pumped flow: | 102.85 | L/s
850 | d08 | Cost: | €181.07 | Europerday
851 | d08 | Energy: | 1207.15 | kWh/day
852 | d08 | Tank Elevation | 29.74 | m above sea level
853 | d08 | Tank height above ground | 29.74 | m above nearest node
854 | d08 | Tank volume | 1469.6 | m3
855 | d08 | Minimum Pressure | 20.08 | mwc
856 | d08 | Critical Hour | 6 | hrs
857 | d08 | Critical Node | b12 | Node
858 | d08 | Critical Pipes | [] | Unit headloss >10m/km
859 | d08 | Pump Cost | €907,505.33 | Capital Investment
860 | d08 | Tank Cost | €651,548.07 | Capital Investment
861 | d08 | Total Pipe Replacement Cost | €1,413,016.00 | Capital Investment
862 | d08 | Total Investment Cost | €2,972,069.39 | Grand Total
863 | --- | --- | --- | ---
864 | Summary | for | node: | e01
865 | e01 | Duty Head | 34.06 | m
866 | e01 | Duty Flow | 102.81 | L/s
867 | e01 | Actual average pumped flow: | 102.79 | L/s
868 | e01 | Cost: | €164.68 | Europerday
869 | e01 | Energy: | 1097.87 | kWh/day
870 | e01 | Tank Elevation | 26.57 | m above sea level
871 | e01 | Tank height above ground | 26.57 | m above nearest node
872 | e01 | Tank volume | 1469.6 | m3
873 | e01 | Minimum Pressure | 20.1 | mwc
874 | e01 | Critical Hour | 16 | hrs
875 | e01 | Critical Node | b12 | Node
876 | e01 | Critical Pipes | [] | Unit headloss >10m/km
877 | e01 | Pump Cost | €907,505.33 | Capital Investment
878 | e01 | Tank Cost | €637,599.17 | Capital Investment
879 | e01 | Total Pipe Replacement Cost | €1,148,364.00 | Capital Investment
880 | e01 | Total Investment Cost | €2,693,468.49 | Grand Total
881 | --- | --- | --- | ---
882 | Summary | for | node: | e02
883 | e02 | Duty Head | 34.19 | m
884 | e02 | Duty Flow | 102.81 | L/s
885 | e02 | Actual average pumped flow: | 102.76 | L/s
886 | e02 | Cost: | €165.33 | Europerday
887 | e02 | Energy: | 1102.19 | kWh/day
888 | e02 | Tank Elevation | 26.68 | m above sea level
889 | e02 | Tank height above ground | 26.68 | m above nearest node
890 | e02 | Tank volume | 1469.6 | m3
891 | e02 | Minimum Pressure | 20.1 | mwc
892 | e02 | Critical Hour | 16 | hrs
893 | e02 | Critical Node | b12 | Node
894 | e02 | Critical Pipes | [] | Unit headloss >10m/km
895 | e02 | Pump Cost | €907,505.33 | Capital Investment
896 | e02 | Tank Cost | €638,051.81 | Capital Investment
897 | e02 | Total Pipe Replacement Cost | €1,216,584.00 | Capital Investment
898 | e02 | Total Investment Cost | €2,762,141.14 | Grand Total
899 | --- | --- | --- | ---
900 | Summary | for | node: | e03
901 | e03 | Duty Head | 35.19 | m
902 | e03 | Duty Flow | 102.81 | L/s
903 | e03 | Actual average pumped flow: | 102.81 | L/s
904 | e03 | Cost: | €169.91 | Europerday
905 | e03 | Energy: | 1132.71 | kWh/day
906 | e03 | Tank Elevation | 27.27 | m above sea level
907 | e03 | Tank height above ground | 27.27 | m above nearest node
908 | e03 | Tank volume | 1469.6 | m3
909 | e03 | Minimum Pressure | 19.91 | mwc
910 | e03 | Critical Hour | 16 | hrs
911 | e03 | Critical Node | b12 | Node
912 | e03 | Critical Pipes | [] | Unit headloss >10m/km
913 | e03 | Pump Cost | €907,505.33 | Capital Investment
914 | e03 | Tank Cost | €640,681.32 | Capital Investment
915 | e03 | Total Pipe Replacement Cost | €1,287,324.00 | Capital Investment
916 | e03 | Total Investment Cost | €2,835,510.64 | Grand Total
917 | --- | --- | --- | ---
918 | Summary | for | node: | e04
919 | e04 | Duty Head | 36.05 | m
920 | e04 | Duty Flow | 102.81 | L/s
921 | e04 | Actual average pumped flow: | 102.72 | L/s
922 | e04 | Cost: | €173.93 | Europerday
923 | e04 | Energy: | 1159.54 | kWh/day
924 | e04 | Tank Elevation | 28.12 | m above sea level
925 | e04 | Tank height above ground | 28.12 | m above nearest node
926 | e04 | Tank volume | 1469.6 | m3
927 | e04 | Minimum Pressure | 20.1 | mwc
928 | e04 | Critical Hour | 6 | hrs
929 | e04 | Critical Node | b12 | Node
930 | e04 | Critical Pipes | [] | Unit headloss >10m/km
931 | e04 | Pump Cost | €907,505.33 | Capital Investment
932 | e04 | Tank Cost | €644,428.06 | Capital Investment
933 | e04 | Total Pipe Replacement Cost | €1,417,614.00 | Capital Investment
934 | e04 | Total Investment Cost | €2,969,547.39 | Grand Total
935 | --- | --- | --- | ---
936 | Summary | for | node: | e05
937 | e05 | Duty Head | 37.38 | m
938 | e05 | Duty Flow | 102.81 | L/s
939 | e05 | Actual average pumped flow: | 102.85 | L/s
940 | e05 | Cost: | €180.27 | Europerday
941 | e05 | Energy: | 1201.83 | kWh/day
942 | e05 | Tank Elevation | 29.31 | m above sea level
943 | e05 | Tank height above ground | 29.31 | m above nearest node
944 | e05 | Tank volume | 1469.6 | m3
945 | e05 | Minimum Pressure | 20.08 | mwc
946 | e05 | Critical Hour | 6 | hrs
947 | e05 | Critical Node | b12 | Node
948 | e05 | Critical Pipes | [] | Unit headloss >10m/km
949 | e05 | Pump Cost | €907,505.33 | Capital Investment
950 | e05 | Tank Cost | €649,678.42 | Capital Investment
951 | e05 | Total Pipe Replacement Cost | €1,449,198.00 | Capital Investment
952 | e05 | Total Investment Cost | €3,006,381.75 | Grand Total
953 | --- | --- | --- | ---
954 | Summary | for | node: | e06
955 | e06 | Duty Head | 35.02 | m
956 | e06 | Duty Flow | 102.81 | L/s
957 | e06 | Actual average pumped flow: | 102.78 | L/s
958 | e06 | Cost: | €169.16 | Europerday
959 | e06 | Energy: | 1127.75 | kWh/day
960 | e06 | Tank Elevation | 27.4 | m above sea level
961 | e06 | Tank height above ground | 27.4 | m above nearest node
962 | e06 | Tank volume | 1469.6 | m3
963 | e06 | Minimum Pressure | 20.1 | mwc
964 | e06 | Critical Hour | 16 | hrs
965 | e06 | Critical Node | b12 | Node
966 | e06 | Critical Pipes | [] | Unit headloss >10m/km
967 | e06 | Pump Cost | €907,505.33 | Capital Investment
968 | e06 | Tank Cost | €641,230.30 | Capital Investment
969 | e06 | Total Pipe Replacement Cost | €1,466,163.00 | Capital Investment
970 | e06 | Total Investment Cost | €3,014,898.63 | Grand Total
971 | --- | --- | --- | ---
972 | Summary | for | node: | e07
973 | e07 | Duty Head | 35.8 | m
974 | e07 | Duty Flow | 102.81 | L/s
975 | e07 | Actual average pumped flow: | 102.81 | L/s
976 | e07 | Cost: | €172.79 | Europerday
977 | e07 | Energy: | 1151.93 | kWh/day
978 | e07 | Tank Elevation | 27.82 | m above sea level
979 | e07 | Tank height above ground | 27.82 | m above nearest node
980 | e07 | Tank volume | 1469.6 | m3
981 | e07 | Minimum Pressure | 19.97 | mwc
982 | e07 | Critical Hour | 6 | hrs
983 | e07 | Critical Node | b12 | Node
984 | e07 | Critical Pipes | [] | Unit headloss >10m/km
985 | e07 | Pump Cost | €907,505.33 | Capital Investment
986 | e07 | Tank Cost | €643,102.56 | Capital Investment
987 | e07 | Total Pipe Replacement Cost | €1,496,404.00 | Capital Investment
988 | e07 | Total Investment Cost | €3,047,011.89 | Grand Total
989 | --- | --- | --- | ---
990 | Summary | for | node: | e08
991 | e08 | Duty Head | 36.47 | m
992 | e08 | Duty Flow | 102.81 | L/s
993 | e08 | Actual average pumped flow: | 102.74 | L/s
994 | e08 | Cost: | €175.91 | Europerday
995 | e08 | Energy: | 1172.75 | kWh/day
996 | e08 | Tank Elevation | 28.48 | m above sea level
997 | e08 | Tank height above ground | 28.48 | m above nearest node
998 | e08 | Tank volume | 1469.6 | m3
999 | e08 | Minimum Pressure | 20.1 | mwc
1000 | e08 | Critical Hour | 6 | hrs
1001 | e08 | Critical Node | b12 | Node
1002 | e08 | Critical Pipes | [] | Unit headloss >10m/km
1003 | e08 | Pump Cost | €907,505.33 | Capital Investment
1004 | e08 | Tank Cost | €646,017.16 | Capital Investment
1005 | e08 | Total Pipe Replacement Cost | €1,593,189.00 | Capital Investment
1006 | e08 | Total Investment Cost | €3,146,711.49 | Grand Total
1007 | --- | --- | --- | ---
1008 | Summary | for | node: | f01
1009 | f01 | Duty Head | 34.44 | m
1010 | f01 | Duty Flow | 102.81 | L/s
1011 | f01 | Actual average pumped flow: | 102.78 | L/s
1012 | f01 | Cost: | €166.44 | Europerday
1013 | f01 | Energy: | 1109.63 | kWh/day
1014 | f01 | Tank Elevation | 26.82 | m above sea level
1015 | f01 | Tank height above ground | 26.82 | m above nearest node
1016 | f01 | Tank volume | 1469.6 | m3
1017 | f01 | Minimum Pressure | 20.1 | mwc
1018 | f01 | Critical Hour | 16 | hrs
1019 | f01 | Critical Node | b12 | Node
1020 | f01 | Critical Pipes | [] | Unit headloss >10m/km
1021 | f01 | Pump Cost | €907,505.33 | Capital Investment
1022 | f01 | Tank Cost | €638,698.18 | Capital Investment
1023 | f01 | Total Pipe Replacement Cost | €1,423,724.00 | Capital Investment
1024 | f01 | Total Investment Cost | €2,969,927.51 | Grand Total
1025 | --- | --- | --- | ---

## a01
This sheet contains the results for tank connected to node: a01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.57 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | e05
Cost: | €225.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1502.89 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 42.62 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 42.62 | m above nearest node |  | Tank Cost | €708,340.50
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,141,879.83
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a02
This sheet contains the results for tank connected to node: a02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.58 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €215.78 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1438.55 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 39.57 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 39.57 | m above nearest node |  | Tank Cost | €694,890.21
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,128,429.53
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a03
This sheet contains the results for tank connected to node: a03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.17 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €213.81 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1425.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 39.02 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 39.02 | m above nearest node |  | Tank Cost | €692,488.29
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €701,174.00
|  |  |  | Total Investment Cost | €2,301,167.61
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.3 | 270 | 102600
p05 | 0.08 | 325 | 0.25 | 225 | 73125
p07 | 0.08 | 249 | 0.25 | 225 | 56025
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a04
This sheet contains the results for tank connected to node: a04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.58 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €210.96 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1406.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.04 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 38.04 | m above nearest node |  | Tank Cost | €688,136.32
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,121,675.65
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a05
This sheet contains the results for tank connected to node: a05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.62 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | €211.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1407.77 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.21 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 38.21 | m above nearest node |  | Tank Cost | €688,891.78
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €695,279.00
|  |  |  | Total Investment Cost | €2,291,676.11
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.25 | 225 | 85500
p05 | 0.08 | 325 | 0.25 | 225 | 73125
p07 | 0.08 | 249 | 0.3 | 270 | 67230
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a06
This sheet contains the results for tank connected to node: a06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.12 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €208.71 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1391.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.33 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 37.33 | m above nearest node |  | Tank Cost | €685,018.03
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,118,557.36
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a07
This sheet contains the results for tank connected to node: a07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.82 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €207.26 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1381.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.87 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.87 | m above nearest node |  | Tank Cost | €682,991.43
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,116,530.76
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a08
This sheet contains the results for tank connected to node: a08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.74 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | €206.89 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1379.28 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.77 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.77 | m above nearest node |  | Tank Cost | €682,568.77
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €790,869.00
|  |  |  | Total Investment Cost | €2,380,943.10
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.2 | 180 | 36000
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p12 | 0.08 | 106 | 0.1 | 90 | 9540
p13 | 0.08 | 215 | 0.1 | 90 | 19350
p16 | 0.025 | 168 | 0.05 | 45 | 7560
p18 | 0.1 | 420 | 0.2 | 180 | 75600
p19 | 0.1 | 459 | 0.25 | 225 | 103275
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a09
This sheet contains the results for tank connected to node: a09
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | €208.03 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1386.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.87 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.87 | m above nearest node |  | Tank Cost | €682,981.52
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €833,700.00
|  |  |  | Total Investment Cost | €2,424,186.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.3 | 270 | 69120
p10 | 0.1 | 200 | 0.3 | 270 | 54000
p11 | 0.08 | 111 | 0.2 | 180 | 19980
p12 | 0.08 | 106 | 0.15 | 135 | 14310
p13 | 0.08 | 215 | 0.15 | 135 | 29025
p16 | 0.025 | 168 | 0.08 | 72 | 12096
p18 | 0.1 | 420 | 0.25 | 225 | 94500
p19 | 0.1 | 459 | 0.25 | 225 | 103275
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a10
This sheet contains the results for tank connected to node: a10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.8 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.8 | L/s |  | Critical Node | e05
Cost: | €207.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1380.41 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.76 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.76 | m above nearest node |  | Tank Cost | €682,504.44
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €890,584.00
|  |  |  | Total Investment Cost | €2,480,593.77
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.125 | 110 | 22000
p11 | 0.08 | 111 | 0.4 | 360 | 39960
p12 | 0.08 | 106 | 0.2 | 180 | 19080
p13 | 0.08 | 215 | 0.2 | 180 | 38700
p14 | 0.08 | 369 | 0.1 | 90 | 33210
p15 | 0.08 | 386 | 0.1 | 90 | 34740
p16 | 0.025 | 168 | 0.1 | 90 | 15120
p18 | 0.1 | 420 | 0.2 | 180 | 75600
p19 | 0.1 | 459 | 0.2 | 180 | 82620
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a11
This sheet contains the results for tank connected to node: a11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.6 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | e05
Cost: | €210.96 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1406.39 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.5 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 37.5 | m above nearest node |  | Tank Cost | €685,759.83
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €901,659.00
|  |  |  | Total Investment Cost | €2,494,924.16
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.3 | 270 | 69120
p10 | 0.1 | 200 | 0.2 | 180 | 36000
p11 | 0.08 | 111 | 0.25 | 225 | 24975
p12 | 0.08 | 106 | 0.25 | 225 | 23850
p13 | 0.08 | 215 | 0.25 | 225 | 48375
p14 | 0.08 | 369 | 0.1 | 90 | 33210
p15 | 0.08 | 386 | 0.1 | 90 | 34740
p16 | 0.025 | 168 | 0.1 | 90 | 15120
p18 | 0.1 | 420 | 0.2 | 180 | 75600
p19 | 0.1 | 459 | 0.25 | 225 | 103275
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a12
This sheet contains the results for tank connected to node: a12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 43.96 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €212.71 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1418.09 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 37.94 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 37.94 | m above nearest node |  | Tank Cost | €687,727.54
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €942,969.00
|  |  |  | Total Investment Cost | €2,538,201.87
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.15 | 135 | 27000
p11 | 0.08 | 111 | 0.3 | 270 | 29970
p12 | 0.08 | 106 | 0.2 | 180 | 19080
p13 | 0.08 | 215 | 0.1 | 90 | 19350
p14 | 0.08 | 369 | 0.3 | 270 | 99630
p15 | 0.08 | 386 | 0.2 | 180 | 69480
p16 | 0.025 | 168 | 0.2 | 180 | 30240
p18 | 0.1 | 420 | 0.15 | 135 | 56700
p19 | 0.1 | 459 | 0.15 | 135 | 61965
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a13
This sheet contains the results for tank connected to node: a13
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 44.2 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €213.77 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1425.13 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 38.12 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 38.12 | m above nearest node |  | Tank Cost | €688,490.89
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,002,279.00
|  |  |  | Total Investment Cost | €2,598,275.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.4 | 360 | 92160
p10 | 0.1 | 200 | 0.25 | 225 | 45000
p11 | 0.08 | 111 | 0.25 | 225 | 24975
p12 | 0.08 | 106 | 0.25 | 225 | 23850
p13 | 0.08 | 215 | 0.2 | 180 | 38700
p14 | 0.08 | 369 | 0.2 | 180 | 66420
p15 | 0.08 | 386 | 0.3 | 270 | 104220
p16 | 0.025 | 168 | 0.2 | 180 | 30240
p18 | 0.1 | 420 | 0.15 | 135 | 56700
p19 | 0.1 | 459 | 0.2 | 180 | 82620
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a14
This sheet contains the results for tank connected to node: a14
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.99 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €203.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1355.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35.6 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 35.6 | m above nearest node |  | Tank Cost | €677,414.25
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,110,953.58
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a15
This sheet contains the results for tank connected to node: a15
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42.78 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.73 | L/s |  | Critical Node | e05
Cost: | €207.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1380.4 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 36.55 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 36.55 | m above nearest node |  | Tank Cost | €681,594.94
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €813,504.00
|  |  |  | Total Investment Cost | €2,402,604.27
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.25 | 225 | 57600
p10 | 0.1 | 200 | 0.25 | 225 | 45000
p11 | 0.08 | 111 | 0.125 | 110 | 12210
p12 | 0.08 | 106 | 0.125 | 110 | 11660
p13 | 0.08 | 215 | 0.125 | 110 | 23650
p16 | 0.025 | 168 | 0.05 | 45 | 7560
p18 | 0.1 | 420 | 0.25 | 225 | 94500
p19 | 0.1 | 459 | 0.3 | 270 | 123930
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a16
This sheet contains the results for tank connected to node: a16
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.79 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €202.26 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1348.42 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35.27 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 35.27 | m above nearest node |  | Tank Cost | €675,938.21
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €526,034.00
|  |  |  | Total Investment Cost | €2,109,477.54
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a17
This sheet contains the results for tank connected to node: a17
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.09 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | €198.90 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1325.99 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 34.5 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 34.5 | m above nearest node |  | Tank Cost | €672,548.31
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €695,444.00
|  |  |  | Total Investment Cost | €2,275,497.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.3 | 270 | 45360
p22 | 0.08 | 291 | 0.125 | 110 | 32010
p24 | 0.08 | 255 | 0.2 | 180 | 45900
p25 | 0.05 | 206 | 0.125 | 110 | 22660
p26 | 0.1 | 202 | 0.2 | 180 | 36360
p27 | 0.08 | 289 | 0.125 | 110 | 31790
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a18
This sheet contains the results for tank connected to node: a18
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 41.73 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €201.85 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1345.67 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 35 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 35 | m above nearest node |  | Tank Cost | €674,742.30
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €730,754.00
|  |  |  | Total Investment Cost | €2,313,001.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.3 | 270 | 45360
p22 | 0.08 | 291 | 0.3 | 270 | 78570
p25 | 0.05 | 206 | 0.2 | 180 | 37080
p26 | 0.1 | 202 | 0.2 | 180 | 36360
p27 | 0.08 | 289 | 0.2 | 180 | 52020
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a19
This sheet contains the results for tank connected to node: a19
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.54 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €191.32 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1275.49 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 32.75 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 32.75 | m above nearest node |  | Tank Cost | €664,811.36
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €628,994.00
|  |  |  | Total Investment Cost | €2,201,310.69
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a20
This sheet contains the results for tank connected to node: a20
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 39.76 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | e05
Cost: | €192.40 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1282.69 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 33.08 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 33.08 | m above nearest node |  | Tank Cost | €666,282.10
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €823,739.00
|  |  |  | Total Investment Cost | €2,397,526.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.25 | 225 | 37800
p22 | 0.08 | 291 | 0.125 | 110 | 32010
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.25 | 225 | 57375
p25 | 0.05 | 206 | 0.125 | 110 | 22660
p26 | 0.1 | 202 | 0.3 | 270 | 54540
p27 | 0.08 | 289 | 0.125 | 110 | 31790
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## a21
This sheet contains the results for tank connected to node: a21
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.09 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €194.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1293.46 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 33.43 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 33.43 | m above nearest node |  | Tank Cost | €667,817.26
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €892,709.00
|  |  |  | Total Investment Cost | €2,468,031.59
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.25 | 225 | 37800
p22 | 0.08 | 291 | 0.25 | 225 | 65475
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p25 | 0.05 | 206 | 0.25 | 225 | 46350
p26 | 0.1 | 202 | 0.3 | 270 | 54540
p27 | 0.08 | 289 | 0.3 | 270 | 78030
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b01
This sheet contains the results for tank connected to node: b01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.16 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | e05
Cost: | €179.83 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1198.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.1 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.1 | m above nearest node |  | Tank Cost | €653,165.04
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €762,914.00
|  |  |  | Total Investment Cost | €2,323,584.37
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b02
This sheet contains the results for tank connected to node: b02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.29 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.72 | L/s |  | Critical Node | e05
Cost: | €180.42 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1202.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.17 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.17 | m above nearest node |  | Tank Cost | €653,460.44
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €901,514.00
|  |  |  | Total Investment Cost | €2,462,479.77
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b03
This sheet contains the results for tank connected to node: b03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.41 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €180.97 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1206.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.17 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.17 | m above nearest node |  | Tank Cost | €653,475.24
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €990,794.00
|  |  |  | Total Investment Cost | €2,551,774.57
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b04
This sheet contains the results for tank connected to node: b04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.55 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | e05
Cost: | €181.61 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1210.74 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.31 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.31 | m above nearest node |  | Tank Cost | €654,079.77
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,123,368.00
|  |  |  | Total Investment Cost | €2,684,953.10
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.4 | 360 | 100080
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.1 | 90 | 26100
p36 | 0.05 | 269 | 0.1 | 90 | 24210
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b05
This sheet contains the results for tank connected to node: b05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.37 | m |  | Minimum Pressure | 19.95 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €185.41 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1236.1 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.92 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.92 | m above nearest node |  | Tank Cost | €656,758.23
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,230,660.00
|  |  |  | Total Investment Cost | €2,794,923.56
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.3 | 270 | 75060
p32 | 0.125 | 270 | 0.3 | 270 | 72900
p33 | 0.08 | 106 | 0.125 | 110 | 11660
p34 | 0.05 | 290 | 0.125 | 110 | 31900
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.125 | 110 | 29590
p37 | 0.05 | 333 | 0.125 | 110 | 36630
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b06
This sheet contains the results for tank connected to node: b06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.62 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €181.93 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1212.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.36 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.36 | m above nearest node |  | Tank Cost | €654,282.57
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,175,820.00
|  |  |  | Total Investment Cost | €2,737,607.89
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.125 | 110 | 11660
p34 | 0.05 | 290 | 0.125 | 110 | 31900
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.125 | 110 | 36630
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p39 | 0.125 | 380 | 0.4 | 360 | 136800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b07
This sheet contains the results for tank connected to node: b07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.34 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €185.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1235.26 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.94 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.94 | m above nearest node |  | Tank Cost | €656,852.15
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,195,773.00
|  |  |  | Total Investment Cost | €2,760,130.47
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p32 | 0.125 | 270 | 0.15 | 135 | 36450
p33 | 0.08 | 106 | 0.3 | 270 | 28620
p34 | 0.05 | 290 | 0.15 | 135 | 39150
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.15 | 135 | 44955
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p39 | 0.125 | 380 | 0.3 | 270 | 102600
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b08
This sheet contains the results for tank connected to node: b08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.67 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | e05
Cost: | €186.82 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1245.47 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.25 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31.25 | m above nearest node |  | Tank Cost | €658,217.49
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,321,665.00
|  |  |  | Total Investment Cost | €2,887,387.82
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.25 | 225 | 62550
p32 | 0.125 | 270 | 0.25 | 225 | 60750
p33 | 0.08 | 106 | 0.25 | 225 | 23850
p34 | 0.05 | 290 | 0.25 | 225 | 65250
p36 | 0.05 | 269 | 0.1 | 90 | 24210
p37 | 0.05 | 333 | 0.25 | 225 | 74925
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p39 | 0.125 | 380 | 0.25 | 225 | 85500
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b09
This sheet contains the results for tank connected to node: b09
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.59 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €181.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1211.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 30.34 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 30.34 | m above nearest node |  | Tank Cost | €654,219.18
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,175,778.00
|  |  |  | Total Investment Cost | €2,737,502.51
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.125 | 110 | 29590
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p40 | 0.125 | 289 | 0.4 | 360 | 104040
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b10
This sheet contains the results for tank connected to node: b10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.34 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | e05
Cost: | €185.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1235.28 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31 | m above nearest node |  | Tank Cost | €657,119.84
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,180,008.00
|  |  |  | Total Investment Cost | €2,744,633.17
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.125 | 110 | 29590
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.125 | 110 | 41800
p40 | 0.125 | 289 | 0.3 | 270 | 78030
p41 | 0.125 | 112 | 0.3 | 270 | 30240
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b11
This sheet contains the results for tank connected to node: b11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 40.13 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | e05
Cost: | €193.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1290.91 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 32.17 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 32.17 | m above nearest node |  | Tank Cost | €662,259.66
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,231,931.00
|  |  |  | Total Investment Cost | €2,801,695.99
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.3 | 270 | 101520
p30 | 0.2 | 248 | 0.3 | 270 | 66960
p32 | 0.125 | 270 | 0.15 | 135 | 36450
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.3 | 270 | 118530
p36 | 0.05 | 269 | 0.15 | 135 | 36315
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.15 | 135 | 51300
p40 | 0.125 | 289 | 0.3 | 270 | 78030
p41 | 0.125 | 112 | 0.3 | 270 | 30240
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## b12
This sheet contains the results for tank connected to node: b12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 38.68 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | e05
Cost: | €186.88 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1245.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.21 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31.21 | m above nearest node |  | Tank Cost | €658,026.79
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,415,572.00
|  |  |  | Total Investment Cost | €2,981,104.11
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p29 | 0.2 | 376 | 0.4 | 360 | 135360
p30 | 0.2 | 248 | 0.4 | 360 | 89280
p31 | 0.15 | 278 | 0.3 | 270 | 75060
p32 | 0.125 | 270 | 0.3 | 270 | 72900
p33 | 0.08 | 106 | 0.125 | 110 | 11660
p34 | 0.05 | 290 | 0.1 | 90 | 26100
p35 | 0.1 | 439 | 0.2 | 180 | 79020
p36 | 0.05 | 269 | 0.2 | 180 | 48420
p37 | 0.05 | 333 | 0.1 | 90 | 29970
p38 | 0.08 | 380 | 0.3 | 270 | 102600
p40 | 0.125 | 289 | 0.2 | 180 | 52020
p41 | 0.125 | 112 | 0.2 | 180 | 20160
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c01
This sheet contains the results for tank connected to node: c01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €164.41 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1096.04 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.57 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.57 | m above nearest node |  | Tank Cost | €637,571.18
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,049,974.00
|  |  |  | Total Investment Cost | €2,595,050.51
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c02
This sheet contains the results for tank connected to node: c02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.09 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | b12
Cost: | €164.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1098.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.65 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.65 | m above nearest node |  | Tank Cost | €637,940.03
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,198,284.00
|  |  |  | Total Investment Cost | €2,743,729.36
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.125 | 110 | 17490
p56 | 0.1 | 349 | 0.125 | 110 | 38390
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c03
This sheet contains the results for tank connected to node: c03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.74 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €167.85 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1119.03 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.16 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.16 | m above nearest node |  | Tank Cost | €640,173.89
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,269,619.00
|  |  |  | Total Investment Cost | €2,817,298.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p53 | 0.1 | 177 | 0.3 | 270 | 47790
p54 | 0.08 | 177 | 0.15 | 135 | 23895
p55 | 0.08 | 159 | 0.15 | 135 | 21465
p56 | 0.1 | 349 | 0.15 | 135 | 47115
p57 | 0.125 | 108 | 0.2 | 180 | 19440
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c04
This sheet contains the results for tank connected to node: c04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.91 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €168.69 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1124.6 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.33 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.33 | m above nearest node |  | Tank Cost | €640,915.06
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,332,844.00
|  |  |  | Total Investment Cost | €2,881,264.38
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p53 | 0.1 | 177 | 0.3 | 270 | 47790
p54 | 0.08 | 177 | 0.3 | 270 | 47790
p55 | 0.08 | 159 | 0.2 | 180 | 28620
p56 | 0.1 | 349 | 0.2 | 180 | 62820
p57 | 0.125 | 108 | 0.2 | 180 | 19440
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.25 | 225 | 82350
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c05
This sheet contains the results for tank connected to node: c05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.22 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €165.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1102.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.67 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.67 | m above nearest node |  | Tank Cost | €638,022.14
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,296,246.00
|  |  |  | Total Investment Cost | €2,841,773.47
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p25 | 0.05 | 206 | 0.08 | 72 | 14832
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p53 | 0.1 | 177 | 0.125 | 110 | 19470
p54 | 0.08 | 177 | 0.125 | 110 | 19470
p55 | 0.08 | 159 | 0.125 | 110 | 17490
p56 | 0.1 | 349 | 0.125 | 110 | 38390
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.4 | 360 | 131760
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c06
This sheet contains the results for tank connected to node: c06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €169.03 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1126.89 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.11 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.11 | m above nearest node |  | Tank Cost | €639,955.10
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,317,184.00
|  |  |  | Total Investment Cost | €2,864,644.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.2 | 180 | 33120
p53 | 0.1 | 177 | 0.15 | 135 | 23895
p54 | 0.08 | 177 | 0.15 | 135 | 23895
p55 | 0.08 | 159 | 0.15 | 135 | 21465
p56 | 0.1 | 349 | 0.15 | 135 | 47115
p57 | 0.125 | 108 | 0.3 | 270 | 29160
p58 | 0.25 | 168 | 0.3 | 270 | 45360
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.3 | 270 | 98820
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## c07
This sheet contains the results for tank connected to node: c07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.38 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.77 | L/s |  | Critical Node | b12
Cost: | €170.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1138.92 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.56 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.56 | m above nearest node |  | Tank Cost | €641,962.19
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,336,354.00
|  |  |  | Total Investment Cost | €2,885,821.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.25 | 225 | 41400
p53 | 0.1 | 177 | 0.25 | 225 | 39825
p54 | 0.08 | 177 | 0.25 | 225 | 39825
p55 | 0.08 | 159 | 0.25 | 225 | 35775
p56 | 0.1 | 349 | 0.25 | 225 | 78525
p57 | 0.125 | 108 | 0.25 | 225 | 24300
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.25 | 225 | 82350
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d01
This sheet contains the results for tank connected to node: d01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.22 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €165.46 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1103.05 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.75 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.75 | m above nearest node |  | Tank Cost | €638,392.26
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,229,074.00
|  |  |  | Total Investment Cost | €2,774,971.58
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p44 | 0.15 | 201 | 0.4 | 360 | 72360
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d02
This sheet contains the results for tank connected to node: d02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.79 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | b12
Cost: | €172.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1152.27 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.15 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.15 | m above nearest node |  | Tank Cost | €644,542.28
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,226,014.00
|  |  |  | Total Investment Cost | €2,778,061.61
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p45 | 0.05 | 214 | 0.3 | 270 | 57780
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d03
This sheet contains the results for tank connected to node: d03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.34 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | b12
Cost: | €166.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1106.78 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.86 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.86 | m above nearest node |  | Tank Cost | €638,849.57
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,322,224.00
|  |  |  | Total Investment Cost | €2,868,578.90
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p44 | 0.15 | 201 | 0.4 | 360 | 72360
p46 | 0.15 | 195 | 0.4 | 360 | 70200
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d04
This sheet contains the results for tank connected to node: d04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 42 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.87 | L/s |  | Critical Node | b12
Cost: | €202.09 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1347.27 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 31.06 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 31.06 | m above nearest node |  | Tank Cost | €657,371.28
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,150,864.00
|  |  |  | Total Investment Cost | €2,715,740.60
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.3 | 270 | 196290
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.2 | 180 | 24480
p48 | 0.08 | 461 | 0.25 | 225 | 103725
p49 | 0.05 | 148 | 0.15 | 135 | 19980
p50 | 0.1 | 85 | 0.15 | 135 | 11475
p51 | 0.05 | 368 | 0.15 | 135 | 49680
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d05
This sheet contains the results for tank connected to node: d05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €166.43 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1109.53 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.94 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.94 | m above nearest node |  | Tank Cost | €639,206.90
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,438,864.00
|  |  |  | Total Investment Cost | €2,985,576.23
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.4 | 360 | 66240
p44 | 0.15 | 201 | 0.4 | 360 | 72360
p46 | 0.15 | 195 | 0.4 | 360 | 70200
p47 | 0.1 | 136 | 0.4 | 360 | 48960
p48 | 0.08 | 461 | 0.125 | 110 | 50710
p49 | 0.05 | 148 | 0.125 | 110 | 16280
p50 | 0.1 | 85 | 0.125 | 110 | 9350
p51 | 0.05 | 368 | 0.125 | 110 | 40480
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d06
This sheet contains the results for tank connected to node: d06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.41 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.84 | L/s |  | Critical Node | b12
Cost: | €175.77 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1171.81 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.66 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.66 | m above nearest node |  | Tank Cost | €646,798.73
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,414,214.00
|  |  |  | Total Investment Cost | €2,968,518.06
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.3 | 270 | 36720
p48 | 0.08 | 461 | 0.125 | 110 | 50710
p49 | 0.05 | 148 | 0.125 | 110 | 16280
p50 | 0.1 | 85 | 0.3 | 270 | 22950
p51 | 0.05 | 368 | 0.125 | 110 | 40480
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d07
This sheet contains the results for tank connected to node: d07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.03 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.75 | L/s |  | Critical Node | b12
Cost: | €178.64 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1190.94 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 29.32 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 29.32 | m above nearest node |  | Tank Cost | €649,715.93
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,490,434.00
|  |  |  | Total Investment Cost | €3,047,655.26
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.25 | 225 | 30600
p48 | 0.08 | 461 | 0.25 | 225 | 103725
p49 | 0.05 | 148 | 0.25 | 225 | 33300
p50 | 0.1 | 85 | 0.25 | 225 | 19125
p51 | 0.05 | 368 | 0.25 | 225 | 82800
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## d08
This sheet contains the results for tank connected to node: d08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.53 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.85 | L/s |  | Critical Node | b12
Cost: | €181.07 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1207.15 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 29.74 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 29.74 | m above nearest node |  | Tank Cost | €651,548.07
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,413,016.00
|  |  |  | Total Investment Cost | €2,972,069.39
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p43 | 0.15 | 184 | 0.3 | 270 | 49680
p44 | 0.15 | 201 | 0.3 | 270 | 54270
p46 | 0.15 | 195 | 0.3 | 270 | 52650
p47 | 0.1 | 136 | 0.3 | 270 | 36720
p49 | 0.05 | 148 | 0.08 | 72 | 10656
p50 | 0.1 | 85 | 0.3 | 270 | 22950
p51 | 0.05 | 368 | 0.08 | 72 | 26496
p52 | 0.08 | 256 | 0.3 | 270 | 69120
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p55 | 0.08 | 159 | 0.1 | 90 | 14310
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e01
This sheet contains the results for tank connected to node: e01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.06 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.79 | L/s |  | Critical Node | b12
Cost: | €164.68 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1097.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.57 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.57 | m above nearest node |  | Tank Cost | €637,599.17
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,148,364.00
|  |  |  | Total Investment Cost | €2,693,468.49
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p24 | 0.08 | 255 | 0.1 | 90 | 22950
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e02
This sheet contains the results for tank connected to node: e02
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.19 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.76 | L/s |  | Critical Node | b12
Cost: | €165.33 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1102.19 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.68 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.68 | m above nearest node |  | Tank Cost | €638,051.81
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,216,584.00
|  |  |  | Total Investment Cost | €2,762,141.14
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.4 | 360 | 129960
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e03
This sheet contains the results for tank connected to node: e03
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.19 | m |  | Minimum Pressure | 19.91 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €169.91 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1132.71 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.27 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.27 | m above nearest node |  | Tank Cost | €640,681.32
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,287,324.00
|  |  |  | Total Investment Cost | €2,835,510.64
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p66 | 0.05 | 280 | 0.1 | 90 | 25200
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e04
This sheet contains the results for tank connected to node: e04
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.05 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.72 | L/s |  | Critical Node | b12
Cost: | €173.93 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1159.54 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.12 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.12 | m above nearest node |  | Tank Cost | €644,428.06
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,417,614.00
|  |  |  | Total Investment Cost | €2,969,547.39
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p61 | 0.125 | 277 | 0.3 | 270 | 74790
p65 | 0.08 | 272 | 0.1 | 90 | 24480
p66 | 0.05 | 280 | 0.1 | 90 | 25200
p67 | 0.05 | 282 | 0.125 | 110 | 31020
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e05
This sheet contains the results for tank connected to node: e05
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 37.38 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.85 | L/s |  | Critical Node | b12
Cost: | €180.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1201.83 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 29.31 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 29.31 | m above nearest node |  | Tank Cost | €649,678.42
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,449,198.00
|  |  |  | Total Investment Cost | €3,006,381.75
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p61 | 0.125 | 277 | 0.3 | 270 | 74790
p62 | 0.08 | 266 | 0.3 | 270 | 71820
p66 | 0.05 | 280 | 0.08 | 72 | 20160
p67 | 0.05 | 282 | 0.08 | 72 | 20304
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e06
This sheet contains the results for tank connected to node: e06
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.02 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €169.16 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1127.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.4 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.4 | m above nearest node |  | Tank Cost | €641,230.30
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,466,163.00
|  |  |  | Total Investment Cost | €3,014,898.63
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.4 | 360 | 129960
p60 | 0.15 | 289 | 0.2 | 180 | 52020
p63 | 0.1 | 354 | 0.3 | 270 | 95580
p64 | 0.1 | 325 | 0.15 | 135 | 43875
p66 | 0.05 | 280 | 0.15 | 135 | 37800
p67 | 0.05 | 282 | 0.08 | 72 | 20304
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e07
This sheet contains the results for tank connected to node: e07
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 35.8 | m |  | Minimum Pressure | 19.97 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.81 | L/s |  | Critical Node | b12
Cost: | €172.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1151.93 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 27.82 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 27.82 | m above nearest node |  | Tank Cost | €643,102.56
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,496,404.00
|  |  |  | Total Investment Cost | €3,047,011.89
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p63 | 0.1 | 354 | 0.15 | 135 | 47790
p64 | 0.1 | 325 | 0.3 | 270 | 87750
p65 | 0.08 | 272 | 0.125 | 110 | 29920
p66 | 0.05 | 280 | 0.15 | 135 | 37800
p67 | 0.05 | 282 | 0.125 | 110 | 31020
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## e08
This sheet contains the results for tank connected to node: e08
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 36.47 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 6 | hrs
Actual average pumped flow: | 102.74 | L/s |  | Critical Node | b12
Cost: | €175.91 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1172.75 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 28.48 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 28.48 | m above nearest node |  | Tank Cost | €646,017.16
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,593,189.00
|  |  |  | Total Investment Cost | €3,146,711.49
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p22 | 0.08 | 291 | 0.1 | 90 | 26190
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p54 | 0.08 | 177 | 0.1 | 90 | 15930
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.3 | 270 | 97470
p60 | 0.15 | 289 | 0.3 | 270 | 78030
p61 | 0.125 | 277 | 0.25 | 225 | 62325
p63 | 0.1 | 354 | 0.15 | 135 | 47790
p64 | 0.1 | 325 | 0.2 | 180 | 58500
p65 | 0.08 | 272 | 0.25 | 225 | 61200
p66 | 0.05 | 280 | 0.15 | 135 | 37800
p67 | 0.05 | 282 | 0.25 | 225 | 63450
p68 | 0.15 | 366 | 0.2 | 180 | 65880
p69 | 0.15 | 452 | 0.2 | 180 | 81360

## f01
This sheet contains the results for tank connected to node: f01
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 34.44 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 102.81 | L/s |  | Critical Hour | 16 | hrs
Actual average pumped flow: | 102.78 | L/s |  | Critical Node | b12
Cost: | €166.44 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 1109.63 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 26.82 | m above sea level |  | Pump Cost | €907,505.33
Tank height above ground | 26.82 | m above nearest node |  | Tank Cost | €638,698.18
Tank volume | 1469.6 | m3 |  | Total Pipe Replacement Cost | €1,423,724.00
|  |  |  | Total Investment Cost | €2,969,927.51
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
p03 | 0.08 | 380 | 0.1 | 90 | 34200
p07 | 0.08 | 249 | 0.1 | 90 | 22410
p09 | 0.1 | 256 | 0.125 | 110 | 28160
p11 | 0.08 | 111 | 0.1 | 90 | 9990
p19 | 0.1 | 459 | 0.125 | 110 | 50490
p21 | 0.1 | 168 | 0.125 | 110 | 18480
p23 | 0.3 | 295 | 0.4 | 360 | 106200
p28 | 0.3 | 372 | 0.4 | 360 | 133920
p33 | 0.08 | 106 | 0.1 | 90 | 9540
p34 | 0.05 | 290 | 0.08 | 72 | 20880
p35 | 0.1 | 439 | 0.125 | 110 | 48290
p36 | 0.05 | 269 | 0.08 | 72 | 19368
p37 | 0.05 | 333 | 0.08 | 72 | 23976
p38 | 0.08 | 380 | 0.1 | 90 | 34200
p42 | 0.25 | 727 | 0.4 | 360 | 261720
p47 | 0.1 | 136 | 0.125 | 110 | 14960
p53 | 0.1 | 177 | 0.125 | 110 | 19470
p54 | 0.08 | 177 | 0.125 | 110 | 19470
p55 | 0.08 | 159 | 0.125 | 110 | 17490
p56 | 0.1 | 349 | 0.125 | 110 | 38390
p58 | 0.25 | 168 | 0.4 | 360 | 60480
p59 | 0.15 | 361 | 0.2 | 180 | 64980
p60 | 0.15 | 289 | 0.2 | 180 | 52020
p66 | 0.05 | 280 | 0.08 | 72 | 20160
p68 | 0.15 | 366 | 0.4 | 360 | 131760
p69 | 0.15 | 452 | 0.4 | 360 | 162720