## Summary
Summary of results for tank connected to each node
Parameter
Index | Node&Parameter | Node | Parameter | Value | Units | Node | Energy: | Total Investment Cost | Tank Elevation
0 | Summaryfor | Summary | for | node: | 2 | 2 | 4322.2 | 3373366.76 | 57.25
1 | 2Duty Head | 2 | Duty Head | 51.13 | m | 3 | 4270.84 | 3289106.75 | 56.21
2 | 2Duty Flow | 2 | Duty Flow | 269.15 | L/s | 4 | 4208.6 | 3665968.85 | 55.18
3 | 2Actual average pumped flow: | 2 | Actual average pumped flow: | 269.09 | L/s | 5 | 4360.95 | 3394549.04 | 57
4 | 2Cost: | 2 | Cost: | €648.33 | Europerday | 6 | 4172.13 | 3936398.38 | 54.42
5 | 2Energy: | 2 | Energy: | 4322.2 | kWh/day | 7 | 4150.69 | 3760105.48 | 53.54
6 | 2Tank Elevation | 2 | Tank Elevation | 57.25 | m above sea level | 8 | 4301.3 | 3606524.59 | 56.28
7 | 2Tank height above ground | 2 | Tank height above ground | 47.05 | m above nearest node | 9 | 4181.6 | 3620112.36 | 53.9
8 | 2Tank volume | 2 | Tank volume | 3824.63 | m3 | 10 | 4120.56 | 3728805.22 | 52.8
9 | 2Minimum Pressure | 2 | Minimum Pressure | 19.99 | mwc | 11 | 4321.58 | 3770708.88 | 56.46
10 | 2Critical Hour | 2 | Critical Hour | 17 | hrs
11 | 2Critical Node | 2 | Critical Node | 10 | Node |  |  | 1
12 | 2Critical Pipes | 2 | Critical Pipes | [] | Unit headloss >10m/km
13 | 2Pump Cost | 2 | Pump Cost | €1,959,833.05 | Capital Investment
14 | 2Tank Cost | 2 | Tank Cost | €1,413,533.71 | Capital Investment
15 | 2Total Pipe Replacement Cost | 2 | Total Pipe Replacement Cost | €0.00 | Capital Investment
16 | 2Total Investment Cost | 2 | Total Investment Cost | €3,373,366.76 | Grand Total
17 | ------ | --- | --- | --- | ---
18 | Summaryfor | Summary | for | node: | 3
19 | 3Duty Head | 3 | Duty Head | 50.61 | m
20 | 3Duty Flow | 3 | Duty Flow | 269.15 | L/s
21 | 3Actual average pumped flow: | 3 | Actual average pumped flow: | 268.05 | L/s
22 | 3Cost: | 3 | Cost: | €640.63 | Europerday
23 | 3Energy: | 3 | Energy: | 4270.84 | kWh/day
24 | 3Tank Elevation | 3 | Tank Elevation | 56.21 | m above sea level
25 | 3Tank height above ground | 3 | Tank height above ground | 39.71 | m above nearest node
26 | 3Tank volume | 3 | Tank volume | 3824.63 | m3
27 | 3Minimum Pressure | 3 | Minimum Pressure | 19.99 | mwc
28 | 3Critical Hour | 3 | Critical Hour | 18 | hrs
29 | 3Critical Node | 3 | Critical Node | 10 | Node
30 | 3Critical Pipes | 3 | Critical Pipes | [] | Unit headloss >10m/km
31 | 3Pump Cost | 3 | Pump Cost | €1,959,833.05 | Capital Investment
32 | 3Tank Cost | 3 | Tank Cost | €1,329,273.70 | Capital Investment
33 | 3Total Pipe Replacement Cost | 3 | Total Pipe Replacement Cost | €0.00 | Capital Investment
34 | 3Total Investment Cost | 3 | Total Investment Cost | €3,289,106.75 | Grand Total
35 | ------ | --- | --- | --- | ---
36 | Summaryfor | Summary | for | node: | 4
37 | 4Duty Head | 4 | Duty Head | 49.9 | m
38 | 4Duty Flow | 4 | Duty Flow | 269.15 | L/s
39 | 4Actual average pumped flow: | 4 | Actual average pumped flow: | 268.07 | L/s
40 | 4Cost: | 4 | Cost: | €631.29 | Europerday
41 | 4Energy: | 4 | Energy: | 4208.6 | kWh/day
42 | 4Tank Elevation | 4 | Tank Elevation | 55.18 | m above sea level
43 | 4Tank height above ground | 4 | Tank height above ground | 32.08 | m above nearest node
44 | 4Tank volume | 4 | Tank volume | 3824.63 | m3
45 | 4Minimum Pressure | 4 | Minimum Pressure | 20.01 | mwc
46 | 4Critical Hour | 4 | Critical Hour | 18 | hrs
47 | 4Critical Node | 4 | Critical Node | 10 | Node
48 | 4Critical Pipes | 4 | Critical Pipes | [] | Unit headloss >10m/km
49 | 4Pump Cost | 4 | Pump Cost | €1,959,833.05 | Capital Investment
50 | 4Tank Cost | 4 | Tank Cost | €1,241,735.80 | Capital Investment
51 | 4Total Pipe Replacement Cost | 4 | Total Pipe Replacement Cost | €464,400.00 | Capital Investment
52 | 4Total Investment Cost | 4 | Total Investment Cost | €3,665,968.85 | Grand Total
53 | ------ | --- | --- | --- | ---
54 | Summaryfor | Summary | for | node: | 5
55 | 5Duty Head | 5 | Duty Head | 51.64 | m
56 | 5Duty Flow | 5 | Duty Flow | 269.15 | L/s
57 | 5Actual average pumped flow: | 5 | Actual average pumped flow: | 269.1 | L/s
58 | 5Cost: | 5 | Cost: | €654.14 | Europerday
59 | 5Energy: | 5 | Energy: | 4360.95 | kWh/day
60 | 5Tank Elevation | 5 | Tank Elevation | 57 | m above sea level
61 | 5Tank height above ground | 5 | Tank height above ground | 38.7 | m above nearest node
62 | 5Tank volume | 5 | Tank volume | 3824.63 | m3
63 | 5Minimum Pressure | 5 | Minimum Pressure | 20.1 | mwc
64 | 5Critical Hour | 5 | Critical Hour | 17 | hrs
65 | 5Critical Node | 5 | Critical Node | 10 | Node
66 | 5Critical Pipes | 5 | Critical Pipes | [] | Unit headloss >10m/km
67 | 5Pump Cost | 5 | Pump Cost | €1,959,833.05 | Capital Investment
68 | 5Tank Cost | 5 | Tank Cost | €1,317,715.99 | Capital Investment
69 | 5Total Pipe Replacement Cost | 5 | Total Pipe Replacement Cost | €117,000.00 | Capital Investment
70 | 5Total Investment Cost | 5 | Total Investment Cost | €3,394,549.04 | Grand Total
71 | ------ | --- | --- | --- | ---
72 | Summaryfor | Summary | for | node: | 6
73 | 6Duty Head | 6 | Duty Head | 49.4 | m
74 | 6Duty Flow | 6 | Duty Flow | 269.15 | L/s
75 | 6Actual average pumped flow: | 6 | Actual average pumped flow: | 269.06 | L/s
76 | 6Cost: | 6 | Cost: | €625.82 | Europerday
77 | 6Energy: | 6 | Energy: | 4172.13 | kWh/day
78 | 6Tank Elevation | 6 | Tank Elevation | 54.42 | m above sea level
79 | 6Tank height above ground | 6 | Tank height above ground | 31.72 | m above nearest node
80 | 6Tank volume | 6 | Tank volume | 3824.63 | m3
81 | 6Minimum Pressure | 6 | Minimum Pressure | 20.09 | mwc
82 | 6Critical Hour | 6 | Critical Hour | 18 | hrs
83 | 6Critical Node | 6 | Critical Node | 10 | Node
84 | 6Critical Pipes | 6 | Critical Pipes | [] | Unit headloss >10m/km
85 | 6Pump Cost | 6 | Pump Cost | €1,959,833.05 | Capital Investment
86 | 6Tank Cost | 6 | Tank Cost | €1,237,665.33 | Capital Investment
87 | 6Total Pipe Replacement Cost | 6 | Total Pipe Replacement Cost | €738,900.00 | Capital Investment
88 | 6Total Investment Cost | 6 | Total Investment Cost | €3,936,398.38 | Grand Total
89 | ------ | --- | --- | --- | ---
90 | Summaryfor | Summary | for | node: | 7
91 | 7Duty Head | 7 | Duty Head | 49.27 | m
92 | 7Duty Flow | 7 | Duty Flow | 269.15 | L/s
93 | 7Actual average pumped flow: | 7 | Actual average pumped flow: | 268.13 | L/s
94 | 7Cost: | 7 | Cost: | €622.60 | Europerday
95 | 7Energy: | 7 | Energy: | 4150.69 | kWh/day
96 | 7Tank Elevation | 7 | Tank Elevation | 53.54 | m above sea level
97 | 7Tank height above ground | 7 | Tank height above ground | 24.04 | m above nearest node
98 | 7Tank volume | 7 | Tank volume | 3824.63 | m3
99 | 7Minimum Pressure | 7 | Minimum Pressure | 19.97 | mwc
100 | 7Critical Hour | 7 | Critical Hour | 18 | hrs
101 | 7Critical Node | 7 | Critical Node | 10 | Node
102 | 7Critical Pipes | 7 | Critical Pipes | [] | Unit headloss >10m/km
103 | 7Pump Cost | 7 | Pump Cost | €1,959,833.05 | Capital Investment
104 | 7Tank Cost | 7 | Tank Cost | €1,149,572.43 | Capital Investment
105 | 7Total Pipe Replacement Cost | 7 | Total Pipe Replacement Cost | €650,700.00 | Capital Investment
106 | 7Total Investment Cost | 7 | Total Investment Cost | €3,760,105.48 | Grand Total
107 | ------ | --- | --- | --- | ---
108 | Summaryfor | Summary | for | node: | 8
109 | 8Duty Head | 8 | Duty Head | 51.01 | m
110 | 8Duty Flow | 8 | Duty Flow | 269.15 | L/s
111 | 8Actual average pumped flow: | 8 | Actual average pumped flow: | 268.09 | L/s
112 | 8Cost: | 8 | Cost: | €645.19 | Europerday
113 | 8Energy: | 8 | Energy: | 4301.3 | kWh/day
114 | 8Tank Elevation | 8 | Tank Elevation | 56.28 | m above sea level
115 | 8Tank height above ground | 8 | Tank height above ground | 31.88 | m above nearest node
116 | 8Tank volume | 8 | Tank volume | 3824.63 | m3
117 | 8Minimum Pressure | 8 | Minimum Pressure | 20.06 | mwc
118 | 8Critical Hour | 8 | Critical Hour | 17 | hrs
119 | 8Critical Node | 8 | Critical Node | 10 | Node
120 | 8Critical Pipes | 8 | Critical Pipes | [] | Unit headloss >10m/km
121 | 8Pump Cost | 8 | Pump Cost | €1,959,833.05 | Capital Investment
122 | 8Tank Cost | 8 | Tank Cost | €1,239,441.53 | Capital Investment
123 | 8Total Pipe Replacement Cost | 8 | Total Pipe Replacement Cost | €407,250.00 | Capital Investment
124 | 8Total Investment Cost | 8 | Total Investment Cost | €3,606,524.59 | Grand Total
125 | ------ | --- | --- | --- | ---
126 | Summaryfor | Summary | for | node: | 9
127 | 9Duty Head | 9 | Duty Head | 49.63 | m
128 | 9Duty Flow | 9 | Duty Flow | 269.15 | L/s
129 | 9Actual average pumped flow: | 9 | Actual average pumped flow: | 268.13 | L/s
130 | 9Cost: | 9 | Cost: | €627.24 | Europerday
131 | 9Energy: | 9 | Energy: | 4181.6 | kWh/day
132 | 9Tank Elevation | 9 | Tank Elevation | 53.9 | m above sea level
133 | 9Tank height above ground | 9 | Tank height above ground | 22.2 | m above nearest node
134 | 9Tank volume | 9 | Tank volume | 3824.63 | m3
135 | 9Minimum Pressure | 9 | Minimum Pressure | 19.99 | mwc
136 | 9Critical Hour | 9 | Critical Hour | 18 | hrs
137 | 9Critical Node | 9 | Critical Node | 10 | Node
138 | 9Critical Pipes | 9 | Critical Pipes | [] | Unit headloss >10m/km
139 | 9Pump Cost | 9 | Pump Cost | €1,959,833.05 | Capital Investment
140 | 9Tank Cost | 9 | Tank Cost | €1,128,379.31 | Capital Investment
141 | 9Total Pipe Replacement Cost | 9 | Total Pipe Replacement Cost | €531,900.00 | Capital Investment
142 | 9Total Investment Cost | 9 | Total Investment Cost | €3,620,112.36 | Grand Total
143 | ------ | --- | --- | --- | ---
144 | Summaryfor | Summary | for | node: | 10
145 | 10Duty Head | 10 | Duty Head | 48.85 | m
146 | 10Duty Flow | 10 | Duty Flow | 269.15 | L/s
147 | 10Actual average pumped flow: | 10 | Actual average pumped flow: | 269.06 | L/s
148 | 10Cost: | 10 | Cost: | €618.08 | Europerday
149 | 10Energy: | 10 | Energy: | 4120.56 | kWh/day
150 | 10Tank Elevation | 10 | Tank Elevation | 52.8 | m above sea level
151 | 10Tank height above ground | 10 | Tank height above ground | 18.1 | m above nearest node
152 | 10Tank volume | 10 | Tank volume | 3824.63 | m3
153 | 10Minimum Pressure | 10 | Minimum Pressure | 20.1 | mwc
154 | 10Critical Hour | 10 | Critical Hour | 21 | hrs
155 | 10Critical Node | 10 | Critical Node | 10 | Node
156 | 10Critical Pipes | 10 | Critical Pipes | [] | Unit headloss >10m/km
157 | 10Pump Cost | 10 | Pump Cost | €1,959,833.05 | Capital Investment
158 | 10Tank Cost | 10 | Tank Cost | €1,081,372.17 | Capital Investment
159 | 10Total Pipe Replacement Cost | 10 | Total Pipe Replacement Cost | €687,600.00 | Capital Investment
160 | 10Total Investment Cost | 10 | Total Investment Cost | €3,728,805.22 | Grand Total
161 | ------ | --- | --- | --- | ---
162 | Summaryfor | Summary | for | node: | 11
163 | 11Duty Head | 11 | Duty Head | 51.27 | m
164 | 11Duty Flow | 11 | Duty Flow | 269.15 | L/s
165 | 11Actual average pumped flow: | 11 | Actual average pumped flow: | 268.11 | L/s
166 | 11Cost: | 11 | Cost: | €648.24 | Europerday
167 | 11Energy: | 11 | Energy: | 4321.58 | kWh/day
168 | 11Tank Elevation | 11 | Tank Elevation | 56.46 | m above sea level
169 | 11Tank height above ground | 11 | Tank height above ground | 32.46 | m above nearest node
170 | 11Tank volume | 11 | Tank volume | 3824.63 | m3
171 | 11Minimum Pressure | 11 | Minimum Pressure | 20.04 | mwc
172 | 11Critical Hour | 11 | Critical Hour | 17 | hrs
173 | 11Critical Node | 11 | Critical Node | 10 | Node
174 | 11Critical Pipes | 11 | Critical Pipes | [] | Unit headloss >10m/km
175 | 11Pump Cost | 11 | Pump Cost | €1,959,833.05 | Capital Investment
176 | 11Tank Cost | 11 | Tank Cost | €1,246,125.83 | Capital Investment
177 | 11Total Pipe Replacement Cost | 11 | Total Pipe Replacement Cost | €564,750.00 | Capital Investment
178 | 11Total Investment Cost | 11 | Total Investment Cost | €3,770,708.88 | Grand Total
179 | ------ | --- | --- | --- | ---

## 2
This sheet contains the results for tank connected to node: 2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.13 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 269.09 | L/s |  | Critical Node | 10
Cost: | €648.33 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4322.2 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 57.25 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 47.05 | m above nearest node |  | Tank Cost | €1,413,533.71
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €0.00
|  |  |  | Total Investment Cost | €3,373,366.76
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost

## 3
This sheet contains the results for tank connected to node: 3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.61 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.05 | L/s |  | Critical Node | 10
Cost: | €640.63 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4270.84 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.21 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 39.71 | m above nearest node |  | Tank Cost | €1,329,273.70
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €0.00
|  |  |  | Total Investment Cost | €3,289,106.75
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost

## 4
This sheet contains the results for tank connected to node: 4
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.9 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.07 | L/s |  | Critical Node | 10
Cost: | €631.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4208.6 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 55.18 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 32.08 | m above nearest node |  | Tank Cost | €1,241,735.80
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €464,400.00
|  |  |  | Total Investment Cost | €3,665,968.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
3 | 0.4 | 600 | 0.5 | 450 | 270000
10 | 0.15 | 660 | 0.2 | 180 | 118800
12 | 0.15 | 420 | 0.2 | 180 | 75600

## 5
This sheet contains the results for tank connected to node: 5
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.64 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 269.1 | L/s |  | Critical Node | 10
Cost: | €654.14 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4360.95 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 57 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 38.7 | m above nearest node |  | Tank Cost | €1,317,715.99
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €117,000.00
|  |  |  | Total Investment Cost | €3,394,549.04
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
11 | 0.15 | 650 | 0.2 | 180 | 117000

## 6
This sheet contains the results for tank connected to node: 6
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.4 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 269.06 | L/s |  | Critical Node | 10
Cost: | €625.82 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4172.13 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 54.42 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 31.72 | m above nearest node |  | Tank Cost | €1,237,665.33
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €738,900.00
|  |  |  | Total Investment Cost | €3,936,398.38
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
5 | 0.4 | 950 | 0.5 | 450 | 427500
10 | 0.15 | 660 | 0.2 | 180 | 118800
11 | 0.15 | 650 | 0.2 | 180 | 117000
12 | 0.15 | 420 | 0.2 | 180 | 75600

## 7
This sheet contains the results for tank connected to node: 7
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.27 | m |  | Minimum Pressure | 19.97 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.13 | L/s |  | Critical Node | 10
Cost: | €622.60 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4150.69 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 53.54 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 24.04 | m above nearest node |  | Tank Cost | €1,149,572.43
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €650,700.00
|  |  |  | Total Investment Cost | €3,760,105.48
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
6 | 0.3 | 1050 | 0.4 | 360 | 378000
10 | 0.15 | 660 | 0.3 | 270 | 178200
12 | 0.15 | 420 | 0.25 | 225 | 94500

## 8
This sheet contains the results for tank connected to node: 8
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.01 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 268.09 | L/s |  | Critical Node | 10
Cost: | €645.19 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4301.3 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.28 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 31.88 | m above nearest node |  | Tank Cost | €1,239,441.53
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €407,250.00
|  |  |  | Total Investment Cost | €3,606,524.59
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
7 | 0.3 | 580 | 0.5 | 450 | 261000
11 | 0.15 | 650 | 0.25 | 225 | 146250

## 9
This sheet contains the results for tank connected to node: 9
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 49.63 | m |  | Minimum Pressure | 19.99 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 18 | hrs
Actual average pumped flow: | 268.13 | L/s |  | Critical Node | 10
Cost: | €627.24 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4181.6 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 53.9 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 22.2 | m above nearest node |  | Tank Cost | €1,128,379.31
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €531,900.00
|  |  |  | Total Investment Cost | €3,620,112.36
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
8 | 0.3 | 780 | 0.4 | 360 | 280800
11 | 0.15 | 650 | 0.3 | 270 | 175500
12 | 0.15 | 420 | 0.2 | 180 | 75600

## 10
This sheet contains the results for tank connected to node: 10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 48.85 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 269.06 | L/s |  | Critical Node | 10
Cost: | €618.08 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4120.56 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 52.8 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 18.1 | m above nearest node |  | Tank Cost | €1,081,372.17
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €687,600.00
|  |  |  | Total Investment Cost | €3,728,805.22
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
9 | 0.2 | 590 | 0.4 | 360 | 212400
10 | 0.15 | 660 | 0.25 | 225 | 148500
11 | 0.15 | 650 | 0.3 | 270 | 175500
12 | 0.15 | 420 | 0.4 | 360 | 151200

## 11
This sheet contains the results for tank connected to node: 11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.27 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 269.15 | L/s |  | Critical Hour | 17 | hrs
Actual average pumped flow: | 268.11 | L/s |  | Critical Node | 10
Cost: | €648.24 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 4321.58 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 56.46 | m above sea level |  | Pump Cost | €1,959,833.05
Tank height above ground | 32.46 | m above nearest node |  | Tank Cost | €1,246,125.83
Tank volume | 3824.63 | m3 |  | Total Pipe Replacement Cost | €564,750.00
|  |  |  | Total Investment Cost | €3,770,708.88
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter | Cost | Replacement_Cost
7 | 0.3 | 580 | 0.5 | 450 | 261000
11 | 0.15 | 650 | 0.25 | 225 | 146250
13 | 0.2 | 350 | 0.5 | 450 | 157500