## Summary
Summary of results for tank connected to each node
Column1 | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
25 | 1 | 0 | 158.45 | 201.23 | 201.17 | 4205.06 | 10012.04 | 305.95 | 154.95 | 2318.2 | 20.1 | 7 | R_HERA_2 | [] | 1553053.26 | 1725336.88 | 617837.25 | 3896227.39 | 60202.44 | 339690.86 | 1934738.91
22 | R_HERA_2 | 2 | 157.05 | 201.23 | 201.18 | 4167.84 | 9923.43 | 298.1 | 18.1 | 2318.2 | 20.1 | 23 | R_HERA_2 | [] | 1553053.26 | 773608.22 | 24396.33 | 2351057.81 | 52136.71 | 204975.93 | 1778375.18
23 | R_HERA_1 | 2 | 157.04 | 201.23 | 201.17 | 4167.5 | 9922.61 | 298.11 | 28.11 | 2318.2 | 20.1 | 23 | R_HERA_2 | [] | 1553053.26 | 843254.11 | 24396.33 | 2420703.7 | 52693.88 | 211047.98 | 1784878.45
0 | J87 | 4.05 | 154.34 | 201.23 | 201.23 | 4096.39 | 9753.31 | 295.99 | 235.99 | 2318.2 | 20.07 | 23 | R_HERA_2 | [] | 1553053.26 | 2288944.25 | 593440.92 | 4435438.43 | 64589.32 | 386701.73 | 1946472.89
24 | prv1 | 4.05 | 152.07 | 201.23 | 201.18 | 4035.85 | 9609.15 | 296.02 | 236.02 | 2318.2 | 20.1 | 23 | R_HERA_2 | [] | 1553053.26 | 2289121.36 | 812240.31 | 4654414.93 | 65684.73 | 405793.1 | 1944561.28
3 | UNI_HERA_1 | 5.07 | 152.05 | 201.23 | 201.18 | 4035.22 | 9607.66 | 294.72 | 254.72 | 2318.2 | 20.1 | 23 | R_HERA_2 | [] | 1553053.26 | 2419217.15 | 793021.11 | 4765291.52 | 66629.4 | 415459.83 | 1954943.07
18 | J132 | 5.2 | 152.09 | 201.23 | 201.17 | 4036.02 | 9609.57 | 294.68 | 244.68 | 2318.2 | 20.1 | 22 | R_HERA_2 | [] | 1553053.26 | 2349378.47 | 900715.95 | 4803147.68 | 66291.42 | 418760.3 | 1958199.21
15 | UNI_HERA_2 | 5.33 | 152.1 | 201.23 | 201.19 | 4036.06 | 9609.66 | 294.21 | 254.21 | 2318.2 | 20.1 | 22 | R_HERA_2 | [] | 1553053.26 | 2415658.78 | 1073391.79 | 5042103.82 | 66975.35 | 439593.59 | 1979729.63
19 | J133 | 5.51 | 152.06 | 201.23 | 201.17 | 4035.49 | 9608.3 | 294.3 | 254.3 | 2318.2 | 20.1 | 22 | R_HERA_2 | [] | 1553053.26 | 2416284.88 | 1303688.07 | 5273026.21 | 68841.53 | 459726.45 | 2001520.79
1 | HEINEKEN | 5.78 | 152.2 | 201.23 | 201.23 | 4038.79 | 9616.17 | 293.88 | 273.88 | 2318.2 | 20.1 | 22 | R_HERA_2 | [] | 1553053.26 | 2552465.2 | 1465329.48 | 5570847.94 | 68749.98 | 485691.91 | 2028600.44
14 | J99 | 6.11 | 152.2 | 201.23 | 201.16 | 4038.58 | 9615.66 | 293.85 | 273.85 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2552264 | 1681686.26 | 5787003.52 | 69830.15 | 504537.34 | 2048447.53
7 | J92 | 6.17 | 152.18 | 201.23 | 201.18 | 4038.22 | 9614.82 | 294.16 | 264.16 | 2318.2 | 20.1 | 22 | R_HERA_2 | [] | 1553053.26 | 2484866.9 | 1789025.54 | 5826945.7 | 71816.88 | 508019.68 | 2053787.82
13 | J98 | 6.23 | 152.29 | 201.23 | 201.15 | 4041.13 | 9621.74 | 293.79 | 273.79 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2551815.12 | 2003537.66 | 6108406.04 | 71435.82 | 532558.67 | 2079006.58
4 | J89 | 6.27 | 152.24 | 201.23 | 201.23 | 4039.87 | 9618.74 | 293.84 | 283.84 | 2318.2 | 20.09 | 22 | R_HERA_2 | [] | 1553053.26 | 2621706.22 | 1930277.23 | 6105036.71 | 71628.64 | 532264.92 | 2078445.84
12 | J97 | 6.29 | 152.15 | 201.23 | 201.18 | 4037.28 | 9612.57 | 294.06 | 274.06 | 2318.2 | 20.1 | 22 | R_HERA_2 | [] | 1553053.26 | 2553729.08 | 1956625.13 | 6063407.47 | 73205.77 | 528635.49 | 2075448.28
5 | J90 | 6.37 | 152.31 | 201.23 | 201.16 | 4041.35 | 9622.26 | 293.8 | 283.8 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2621445.6 | 2219085.18 | 6393584.03 | 73070.6 | 557421.79 | 2105585.06
17 | J131 | 6.5 | 152.43 | 201.23 | 201.17 | 4044.12 | 9628.86 | 293.79 | 283.79 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2621405.69 | 2373213.1 | 6547672.05 | 73840.92 | 570855.89 | 2120800.64
8 | J93 | 6.61 | 152.47 | 201.23 | 201.23 | 4045.66 | 9632.53 | 293.78 | 283.78 | 2318.2 | 20.09 | 21 | R_HERA_2 | [] | 1553053.26 | 2621301.91 | 2443966.99 | 6618322.16 | 74193.86 | 577015.49 | 2127876.72
20 | CROCODILE_ | 6.69 | 152.31 | 201.23 | 201.23 | 4041.74 | 9623.2 | 293.85 | 283.85 | 2318.2 | 20.08 | 21 | R_HERA_2 | [] | 1553053.26 | 2621821.47 | 2199506.55 | 6374381.28 | 72975.71 | 555747.61 | 2103960.04
9 | J94 | 6.74 | 152.32 | 201.23 | 201.2 | 4041.41 | 9622.41 | 293.89 | 273.89 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2552503.19 | 2357724.43 | 6463280.88 | 75201.46 | 563498.28 | 2113814.96
11 | J96 | 6.91 | 152.5 | 201.23 | 201.17 | 4046.02 | 9633.37 | 293.75 | 273.75 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2551582.51 | 2829196.96 | 6933832.72 | 75562.25 | 604523.13 | 2156881.49
21 | PORT | 6.98 | 152.42 | 201.23 | 201.16 | 4044.23 | 9629.12 | 293.8 | 283.8 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2621434.13 | 2301161.02 | 6475648.41 | 73480.89 | 564576.54 | 2114200.79
10 | J95 | 7.03 | 152.43 | 201.23 | 201.18 | 4044.3 | 9629.29 | 293.74 | 263.74 | 2318.2 | 20.1 | 21 | R_HERA_2 | [] | 1553053.26 | 2481913.83 | 2461366.53 | 6496333.62 | 75472.7 | 566379.97 | 2118022.69
2 | J88 | 7.14 | 152.52 | 201.23 | 201.23 | 4046.81 | 9635.26 | 293.84 | 283.84 | 2318.2 | 20.08 | 21 | R_HERA_2 | [] | 1553053.26 | 2621691.79 | 2617668.89 | 6792413.94 | 75065.49 | 592193.6 | 2144343.86
6 | J91 | 7.2 | 152.63 | 201.23 | 201.23 | 4049.54 | 9641.76 | 293.67 | 263.67 | 2318.2 | 20.08 | 21 | R_HERA_2 | [] | 1553053.26 | 2481444.78 | 2532071.24 | 6566569.28 | 74795.03 | 572503.43 | 2125380.93
16 | PACIFIC_RE | 8.1 | 153.52 | 201.23 | 201.3 | 4073.17 | 9698.03 | 294.59 | 284.59 | 2318.2 | 20.06 | 7 | R_HERA_2 | [] | 1553053.26 | 2626973.96 | 2765189.13 | 6945216.35 | 75845.34 | 605515.61 | 2168069.59
[22 empty] | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc)
[22 empty] | J87 | 4.05 | 154.34 | 201.23 | 201.23 | 4096.39 | 9753.31 | 295.99 | 235.99 | 2318.2 | 20.07
[22 empty] | HEINEKEN | 5.78 | 152.2 | 201.23 | 201.23 | 4038.79 | 9616.17 | 293.88 | 273.88 | 2318.2 | 20.1
[22 empty] | J88 | 7.14 | 152.52 | 201.23 | 201.23 | 4046.81 | 9635.26 | 293.84 | 283.84 | 2318.2 | 20.08
[22 empty] | UNI_HERA_1 | 5.07 | 152.05 | 201.23 | 201.18 | 4035.22 | 9607.66 | 294.72 | 254.72 | 2318.2 | 20.1
[22 empty] | J89 | 6.27 | 152.24 | 201.23 | 201.23 | 4039.87 | 9618.74 | 293.84 | 283.84 | 2318.2 | 20.09
[22 empty] | J90 | 6.37 | 152.31 | 201.23 | 201.16 | 4041.35 | 9622.26 | 293.8 | 283.8 | 2318.2 | 20.1
[22 empty] | J91 | 7.2 | 152.63 | 201.23 | 201.23 | 4049.54 | 9641.76 | 293.67 | 263.67 | 2318.2 | 20.08
[22 empty] | J92 | 6.17 | 152.18 | 201.23 | 201.18 | 4038.22 | 9614.82 | 294.16 | 264.16 | 2318.2 | 20.1
[22 empty] | J93 | 6.61 | 152.47 | 201.23 | 201.23 | 4045.66 | 9632.53 | 293.78 | 283.78 | 2318.2 | 20.09
[22 empty] | J94 | 6.74 | 152.32 | 201.23 | 201.2 | 4041.41 | 9622.41 | 293.89 | 273.89 | 2318.2 | 20.1
[22 empty] | J95 | 7.03 | 152.43 | 201.23 | 201.18 | 4044.3 | 9629.29 | 293.74 | 263.74 | 2318.2 | 20.1
[22 empty] | J96 | 6.91 | 152.5 | 201.23 | 201.17 | 4046.02 | 9633.37 | 293.75 | 273.75 | 2318.2 | 20.1
[22 empty] | J97 | 6.29 | 152.15 | 201.23 | 201.18 | 4037.28 | 9612.57 | 294.06 | 274.06 | 2318.2 | 20.1
[22 empty] | Node | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
[22 empty] | J87 | 23 | R_HERA_2 | [] | 1553053.26 | 2288944.25 | 593440.92 | 4435438.43 | 64589.32 | 386701.73 | 1946472.89
[22 empty] | HEINEKEN | 22 | R_HERA_2 | [] | 1553053.26 | 2552465.2 | 1465329.48 | 5570847.94 | 68749.98 | 485691.91 | 2028600.44
[22 empty] | J88 | 21 | R_HERA_2 | [] | 1553053.26 | 2621691.79 | 2617668.89 | 6792413.94 | 75065.49 | 592193.6 | 2144343.86
[22 empty] | UNI_HERA_1 | 23 | R_HERA_2 | [] | 1553053.26 | 2419217.15 | 793021.11 | 4765291.52 | 66629.4 | 415459.83 | 1954943.07
[22 empty] | J89 | 22 | R_HERA_2 | [] | 1553053.26 | 2621706.22 | 1930277.23 | 6105036.71 | 71628.64 | 532264.92 | 2078445.84
[22 empty] | J90 | 21 | R_HERA_2 | [] | 1553053.26 | 2621445.6 | 2219085.18 | 6393584.03 | 73070.6 | 557421.79 | 2105585.06
[22 empty] | J91 | 21 | R_HERA_2 | [] | 1553053.26 | 2481444.78 | 2532071.24 | 6566569.28 | 74795.03 | 572503.43 | 2125380.93
[22 empty] | J92 | 22 | R_HERA_2 | [] | 1553053.26 | 2484866.9 | 1789025.54 | 5826945.7 | 71816.88 | 508019.68 | 2053787.82
[22 empty] | J93 | 21 | R_HERA_2 | [] | 1553053.26 | 2621301.91 | 2443966.99 | 6618322.16 | 74193.86 | 577015.49 | 2127876.72
[22 empty] | J94 | 21 | R_HERA_2 | [] | 1553053.26 | 2552503.19 | 2357724.43 | 6463280.88 | 75201.46 | 563498.28 | 2113814.96
[22 empty] | J95 | 21 | R_HERA_2 | [] | 1553053.26 | 2481913.83 | 2461366.53 | 6496333.62 | 75472.7 | 566379.97 | 2118022.69
[22 empty] | J96 | 21 | R_HERA_2 | [] | 1553053.26 | 2551582.51 | 2829196.96 | 6933832.72 | 75562.25 | 604523.13 | 2156881.49
[22 empty] | J97 | 22 | R_HERA_2 | [] | 1553053.26 | 2553729.08 | 1956625.13 | 6063407.47 | 73205.77 | 528635.49 | 2075448.28
[22 empty] | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc)
[22 empty] | J98 | 6.23 | 152.29 | 201.23 | 201.15 | 4041.13 | 9621.74 | 293.79 | 273.79 | 2318.2 | 20.1
[22 empty] | J99 | 6.11 | 152.2 | 201.23 | 201.16 | 4038.58 | 9615.66 | 293.85 | 273.85 | 2318.2 | 20.1
[22 empty] | UNI_HERA_2 | 5.33 | 152.1 | 201.23 | 201.19 | 4036.06 | 9609.66 | 294.21 | 254.21 | 2318.2 | 20.1
[22 empty] | PACIFIC_RE | 8.1 | 153.52 | 201.23 | 201.3 | 4073.17 | 9698.03 | 294.59 | 284.59 | 2318.2 | 20.06
[22 empty] | J131 | 6.5 | 152.43 | 201.23 | 201.17 | 4044.12 | 9628.86 | 293.79 | 283.79 | 2318.2 | 20.1
[22 empty] | J132 | 5.2 | 152.09 | 201.23 | 201.17 | 4036.02 | 9609.57 | 294.68 | 244.68 | 2318.2 | 20.1
[22 empty] | J133 | 5.51 | 152.06 | 201.23 | 201.17 | 4035.49 | 9608.3 | 294.3 | 254.3 | 2318.2 | 20.1
[22 empty] | CROCODILE_ | 6.69 | 152.31 | 201.23 | 201.23 | 4041.74 | 9623.2 | 293.85 | 283.85 | 2318.2 | 20.08
[22 empty] | PORT | 6.98 | 152.42 | 201.23 | 201.16 | 4044.23 | 9629.12 | 293.8 | 283.8 | 2318.2 | 20.1
[22 empty] | R_HERA_2 | 2 | 157.05 | 201.23 | 201.18 | 4167.84 | 9923.43 | 298.1 | 18.1 | 2318.2 | 20.1
[22 empty] | R_HERA_1 | 2 | 157.04 | 201.23 | 201.17 | 4167.5 | 9922.61 | 298.11 | 28.11 | 2318.2 | 20.1
[22 empty] | prv1 | 4.05 | 152.07 | 201.23 | 201.18 | 4035.85 | 9609.15 | 296.02 | 236.02 | 2318.2 | 20.1
[22 empty] | 1 | 0 | 158.45 | 201.23 | 201.17 | 4205.06 | 10012.04 | 305.95 | 154.95 | 2318.2 | 20.1
[22 empty] | Node | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
[22 empty] | J98 | 21 | R_HERA_2 | [] | 1553053.26 | 2551815.12 | 2003537.66 | 6108406.04 | 71435.82 | 532558.67 | 2079006.58
[22 empty] | J99 | 21 | R_HERA_2 | [] | 1553053.26 | 2552264 | 1681686.26 | 5787003.52 | 69830.15 | 504537.34 | 2048447.53
[22 empty] | UNI_HERA_2 | 22 | R_HERA_2 | [] | 1553053.26 | 2415658.78 | 1073391.79 | 5042103.82 | 66975.35 | 439593.59 | 1979729.63
[22 empty] | PACIFIC_RE | 7 | R_HERA_2 | [] | 1553053.26 | 2626973.96 | 2765189.13 | 6945216.35 | 75845.34 | 605515.61 | 2168069.59
[22 empty] | J131 | 21 | R_HERA_2 | [] | 1553053.26 | 2621405.69 | 2373213.1 | 6547672.05 | 73840.92 | 570855.89 | 2120800.64
[22 empty] | J132 | 22 | R_HERA_2 | [] | 1553053.26 | 2349378.47 | 900715.95 | 4803147.68 | 66291.42 | 418760.3 | 1958199.21
[22 empty] | J133 | 22 | R_HERA_2 | [] | 1553053.26 | 2416284.88 | 1303688.07 | 5273026.21 | 68841.53 | 459726.45 | 2001520.79
[22 empty] | CROCODILE_ | 21 | R_HERA_2 | [] | 1553053.26 | 2621821.47 | 2199506.55 | 6374381.28 | 72975.71 | 555747.61 | 2103960.04
[22 empty] | PORT | 21 | R_HERA_2 | [] | 1553053.26 | 2621434.13 | 2301161.02 | 6475648.41 | 73480.89 | 564576.54 | 2114200.79
[22 empty] | R_HERA_2 | 23 | R_HERA_2 | [] | 1553053.26 | 773608.22 | 24396.33 | 2351057.81 | 52136.71 | 204975.93 | 1778375.18
[22 empty] | R_HERA_1 | 23 | R_HERA_2 | [] | 1553053.26 | 843254.11 | 24396.33 | 2420703.7 | 52693.88 | 211047.98 | 1784878.45
[22 empty] | prv1 | 23 | R_HERA_2 | [] | 1553053.26 | 2289121.36 | 812240.31 | 4654414.93 | 65684.73 | 405793.1 | 1944561.28
[22 empty] | 1 | 7 | R_HERA_2 | [] | 1553053.26 | 1725336.88 | 617837.25 | 3896227.39 | 60202.44 | 339690.86 | 1934738.91

## J87
This sheet contains the results for tank connected to node: J87
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 154.34 | m |  | Minimum Pressure | 20.07 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,096.39 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9753.31 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 295.99 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 235.99 | m above nearest node |  | Tank Cost | € 2,288,944.25
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 593,440.92
|  |  |  | Total Investment Cost | € 4,435,438.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P174 | 450 | 1705.29 | 500 | 348 | 593440.92

## HEINEKEN
This sheet contains the results for tank connected to node: HEINEKEN
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.2 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,038.79 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9616.17 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.88 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 273.88 | m above nearest node |  | Tank Cost | € 2,552,465.20
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,465,329.48
|  |  |  | Total Investment Cost | € 5,570,847.94
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P141 | 66 | 246.53 | 125 | 34 | 8382.02
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P146 | 54.9 | 450.96 | 200 | 79 | 35625.84
P149 | 110.2 | 228.43 | 200 | 79 | 18045.97
P174 | 450 | 1705.29 | 600 | 462 | 787843.98

## J88
This sheet contains the results for tank connected to node: J88
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.52 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,046.81 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9635.26 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.84 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.84 | m above nearest node |  | Tank Cost | € 2,621,691.79
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,617,668.89
|  |  |  | Total Investment Cost | € 6,792,413.94
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P136 | 220.4 | 895.81 | 500 | 348 | 311741.88
P137 | 220.4 | 298.6 | 500 | 348 | 103912.8
P138 | 198.2 | 292.77 | 500 | 348 | 101883.96
P140 | 141 | 491.38 | 200 | 79 | 38819.02
P141 | 66 | 246.53 | 200 | 79 | 19475.87
P142 | 123.4 | 294.61 | 200 | 79 | 23274.19
P144 | 66 | 266.25 | 225 | 100 | 26625
P145 | 220.4 | 992.43 | 250 | 120 | 119091.6
P146 | 54.9 | 450.96 | 90 | 21 | 9470.16
P149 | 110.2 | 228.43 | 125 | 34 | 7766.62
P166 | 110.2 | 918.75 | 600 | 462 | 424462.5
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 125 | 34 | 30885.94
P193 | 54.9 | 439.45 | 140 | 41 | 18017.45

## UNI_HERA_1
This sheet contains the results for tank connected to node: UNI_HERA_1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.05 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 201.18 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,035.22 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9607.66 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.72 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 254.72 | m above nearest node |  | Tank Cost | € 2,419,217.15
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 793,021.11
|  |  |  | Total Investment Cost | € 4,765,291.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P141 | 66 | 246.53 | 90 | 21 | 5177.13
P174 | 450 | 1705.29 | 600 | 462 | 787843.98

## J89
This sheet contains the results for tank connected to node: J89
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.24 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,039.87 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9618.74 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.84 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.84 | m above nearest node |  | Tank Cost | € 2,621,706.22
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,930,277.23
|  |  |  | Total Investment Cost | € 6,105,036.71
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P134 | 277.6 | 448.9 | 600 | 462 | 207391.8
P135 | 220.4 | 359.13 | 600 | 462 | 165918.06
P141 | 66 | 246.53 | 125 | 34 | 8382.02
P142 | 123.4 | 294.61 | 140 | 41 | 12079.01
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P146 | 54.9 | 450.96 | 225 | 100 | 45096
P149 | 110.2 | 228.43 | 200 | 79 | 18045.97
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 160 | 52 | 47237.32
P193 | 54.9 | 439.45 | 160 | 52 | 22851.4

## J90
This sheet contains the results for tank connected to node: J90
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.31 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.16 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,041.35 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9622.26 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.8 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.8 | m above nearest node |  | Tank Cost | € 2,621,445.60
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,219,085.18
|  |  |  | Total Investment Cost | € 6,393,584.03
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P136 | 220.4 | 895.81 | 500 | 348 | 311741.88
P137 | 220.4 | 298.6 | 500 | 348 | 103912.8
P140 | 141 | 491.38 | 200 | 79 | 38819.02
P141 | 66 | 246.53 | 200 | 79 | 19475.87
P142 | 123.4 | 294.61 | 200 | 79 | 23274.19
P144 | 66 | 266.25 | 250 | 120 | 31950
P145 | 220.4 | 992.43 | 315 | 190 | 188561.7
P146 | 54.9 | 450.96 | 110 | 28 | 12626.88
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 200 | 79 | 71764.39
P193 | 54.9 | 439.45 | 200 | 79 | 34716.55

## J91
This sheet contains the results for tank connected to node: J91
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.63 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,049.54 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9641.76 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.67 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 263.67 | m above nearest node |  | Tank Cost | € 2,481,444.78
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,532,071.24
|  |  |  | Total Investment Cost | € 6,566,569.28
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P136 | 220.4 | 895.81 | 355 | 240 | 214994.4
P137 | 220.4 | 298.6 | 315 | 190 | 56734
P138 | 198.2 | 292.77 | 315 | 190 | 55626.3
P139 | 176.2 | 222.42 | 315 | 190 | 42259.8
P140 | 141 | 491.38 | 315 | 190 | 93362.2
P141 | 66 | 246.53 | 315 | 190 | 46840.7
P142 | 123.4 | 294.61 | 450 | 295 | 86909.95
P143 | 198.2 | 520.83 | 450 | 295 | 153644.85
P144 | 66 | 266.25 | 250 | 120 | 31950
P145 | 220.4 | 992.43 | 450 | 295 | 292766.85
P146 | 54.9 | 450.96 | 200 | 79 | 35625.84
P147 | 277.6 | 191.81 | 400 | 253 | 48527.93
P148 | 277.6 | 1001.38 | 400 | 253 | 253349.14
P149 | 110.2 | 228.43 | 315 | 190 | 43401.7
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 125 | 34 | 30885.94
P193 | 54.9 | 439.45 | 125 | 34 | 14941.3

## J92
This sheet contains the results for tank connected to node: J92
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.18 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.18 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,038.22 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9614.82 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.16 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 264.16 | m above nearest node |  | Tank Cost | € 2,484,866.90
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,789,025.54
|  |  |  | Total Investment Cost | € 5,826,945.70
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P136 | 220.4 | 895.81 | 225 | 100 | 89581
P140 | 141 | 491.38 | 200 | 79 | 38819.02
P141 | 66 | 246.53 | 140 | 41 | 10107.73
P142 | 123.4 | 294.61 | 160 | 52 | 15319.72
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P146 | 54.9 | 450.96 | 250 | 120 | 54115.2
P148 | 277.6 | 1001.38 | 500 | 348 | 348480.24
P149 | 110.2 | 228.43 | 355 | 240 | 54823.2
P150 | 277.6 | 974.01 | 450 | 295 | 287332.95
P151 | 400 | 251.18 | 450 | 295 | 74098.1
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P193 | 54.9 | 439.45 | 75 | 17 | 7470.65

## J93
This sheet contains the results for tank connected to node: J93
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.47 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,045.66 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9632.53 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.78 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.78 | m above nearest node |  | Tank Cost | € 2,621,301.91
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,443,966.99
|  |  |  | Total Investment Cost | € 6,618,322.16
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P136 | 220.4 | 895.81 | 500 | 348 | 311741.88
P137 | 220.4 | 298.6 | 500 | 348 | 103912.8
P138 | 198.2 | 292.77 | 500 | 348 | 101883.96
P139 | 176.2 | 222.42 | 500 | 348 | 77402.16
P140 | 141 | 491.38 | 225 | 100 | 49138
P141 | 66 | 246.53 | 225 | 100 | 24653
P142 | 123.4 | 294.61 | 225 | 100 | 29461
P143 | 198.2 | 520.83 | 250 | 120 | 62499.6
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P145 | 220.4 | 992.43 | 315 | 190 | 188561.7
P146 | 54.9 | 450.96 | 90 | 21 | 9470.16
P149 | 110.2 | 228.43 | 160 | 52 | 11878.36
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 160 | 52 | 47237.32
P193 | 54.9 | 439.45 | 160 | 52 | 22851.4

## J94
This sheet contains the results for tank connected to node: J94
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.32 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.2 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,041.41 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9622.41 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.89 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 273.89 | m above nearest node |  | Tank Cost | € 2,552,503.19
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,357,724.43
|  |  |  | Total Investment Cost | € 6,463,280.88
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P136 | 220.4 | 895.81 | 315 | 190 | 170203.9
P138 | 198.2 | 292.77 | 225 | 100 | 29277
P139 | 176.2 | 222.42 | 225 | 100 | 22242
P140 | 141 | 491.38 | 225 | 100 | 49138
P141 | 66 | 246.53 | 200 | 79 | 19475.87
P142 | 123.4 | 294.61 | 225 | 100 | 29461
P144 | 66 | 266.25 | 315 | 190 | 50587.5
P145 | 220.4 | 992.43 | 500 | 348 | 345365.64
P146 | 54.9 | 450.96 | 250 | 120 | 54115.2
P147 | 277.6 | 191.81 | 450 | 295 | 56583.95
P148 | 277.6 | 1001.38 | 450 | 295 | 295407.1
P149 | 110.2 | 228.43 | 315 | 190 | 43401.7
P150 | 277.6 | 974.01 | 450 | 295 | 287332.95
P151 | 400 | 251.18 | 450 | 295 | 74098.1
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 125 | 34 | 30885.94
P193 | 54.9 | 439.45 | 110 | 28 | 12304.6

## J95
This sheet contains the results for tank connected to node: J95
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.18 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,044.30 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9629.29 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.74 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 263.74 | m above nearest node |  | Tank Cost | € 2,481,913.83
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,461,366.53
|  |  |  | Total Investment Cost | € 6,496,333.62
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P136 | 220.4 | 895.81 | 355 | 240 | 214994.4
P137 | 220.4 | 298.6 | 225 | 100 | 29860
P138 | 198.2 | 292.77 | 250 | 120 | 35132.4
P139 | 176.2 | 222.42 | 250 | 120 | 26690.4
P140 | 141 | 491.38 | 250 | 120 | 58965.6
P141 | 66 | 246.53 | 225 | 100 | 24653
P142 | 123.4 | 294.61 | 250 | 120 | 35353.2
P143 | 198.2 | 520.83 | 500 | 348 | 181248.84
P144 | 66 | 266.25 | 315 | 190 | 50587.5
P145 | 220.4 | 992.43 | 450 | 295 | 292766.85
P146 | 54.9 | 450.96 | 200 | 79 | 35625.84
P147 | 277.6 | 191.81 | 450 | 295 | 56583.95
P148 | 277.6 | 1001.38 | 450 | 295 | 295407.1
P149 | 110.2 | 228.43 | 315 | 190 | 43401.7
P150 | 277.6 | 974.01 | 400 | 253 | 246424.53
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 125 | 34 | 30885.94
P193 | 54.9 | 439.45 | 125 | 34 | 14941.3

## J96
This sheet contains the results for tank connected to node: J96
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.5 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.17 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,046.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9633.37 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.75 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 273.75 | m above nearest node |  | Tank Cost | € 2,551,582.51
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,829,196.96
|  |  |  | Total Investment Cost | € 6,933,832.72
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P136 | 220.4 | 895.81 | 450 | 295 | 264263.95
P137 | 220.4 | 298.6 | 500 | 348 | 103912.8
P138 | 198.2 | 292.77 | 500 | 348 | 101883.96
P139 | 176.2 | 222.42 | 500 | 348 | 77402.16
P140 | 141 | 491.38 | 500 | 348 | 171000.24
P141 | 66 | 246.53 | 315 | 190 | 46840.7
P142 | 123.4 | 294.61 | 315 | 190 | 55975.9
P143 | 198.2 | 520.83 | 315 | 190 | 98957.7
P144 | 66 | 266.25 | 160 | 52 | 13845
P145 | 220.4 | 992.43 | 315 | 190 | 188561.7
P146 | 54.9 | 450.96 | 90 | 21 | 9470.16
P147 | 277.6 | 191.81 | 315 | 190 | 36443.9
P148 | 277.6 | 1001.38 | 315 | 190 | 190262.2
P149 | 110.2 | 228.43 | 200 | 79 | 18045.97
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 160 | 52 | 47237.32
P193 | 54.9 | 439.45 | 160 | 52 | 22851.4

## J97
This sheet contains the results for tank connected to node: J97
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.15 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.18 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,037.28 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9612.57 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.06 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 274.06 | m above nearest node |  | Tank Cost | € 2,553,729.08
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,956,625.13
|  |  |  | Total Investment Cost | € 6,063,407.47
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P136 | 220.4 | 895.81 | 250 | 120 | 107497.2
P138 | 198.2 | 292.77 | 200 | 79 | 23128.83
P139 | 176.2 | 222.42 | 200 | 79 | 17571.18
P140 | 141 | 491.38 | 200 | 79 | 38819.02
P141 | 66 | 246.53 | 160 | 52 | 12819.56
P142 | 123.4 | 294.61 | 200 | 79 | 23274.19
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P146 | 54.9 | 450.96 | 315 | 190 | 85682.4
P147 | 277.6 | 191.81 | 500 | 348 | 66749.88
P148 | 277.6 | 1001.38 | 500 | 348 | 348480.24
P149 | 110.2 | 228.43 | 355 | 240 | 54823.2
P150 | 277.6 | 974.01 | 450 | 295 | 287332.95
P151 | 400 | 251.18 | 450 | 295 | 74098.1
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P193 | 54.9 | 439.45 | 75 | 17 | 7470.65

## J98
This sheet contains the results for tank connected to node: J98
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.29 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.15 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,041.13 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9621.74 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.79 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 273.79 | m above nearest node |  | Tank Cost | € 2,551,815.12
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,003,537.66
|  |  |  | Total Investment Cost | € 6,108,406.04
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P136 | 220.4 | 895.81 | 500 | 348 | 311741.88
P140 | 141 | 491.38 | 200 | 79 | 38819.02
P141 | 66 | 246.53 | 160 | 52 | 12819.56
P142 | 123.4 | 294.61 | 200 | 79 | 23274.19
P144 | 66 | 266.25 | 225 | 100 | 26625
P145 | 220.4 | 992.43 | 250 | 120 | 119091.6
P146 | 54.9 | 450.96 | 90 | 21 | 9470.16
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 160 | 52 | 47237.32
P193 | 54.9 | 439.45 | 160 | 52 | 22851.4

## J99
This sheet contains the results for tank connected to node: J99
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.2 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.16 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,038.58 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9615.66 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.85 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 273.85 | m above nearest node |  | Tank Cost | € 2,552,264.00
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,681,686.26
|  |  |  | Total Investment Cost | € 5,787,003.52
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P134 | 277.6 | 448.9 | 600 | 462 | 207391.8
P141 | 66 | 246.53 | 125 | 34 | 8382.02
P142 | 123.4 | 294.61 | 125 | 34 | 10016.74
P144 | 66 | 266.25 | 160 | 52 | 13845
P146 | 54.9 | 450.96 | 200 | 79 | 35625.84
P149 | 110.2 | 228.43 | 160 | 52 | 11878.36
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P193 | 54.9 | 439.45 | 110 | 28 | 12304.6

## UNI_HERA_2
This sheet contains the results for tank connected to node: UNI_HERA_2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.1 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.19 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,036.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9609.66 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.21 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 254.21 | m above nearest node |  | Tank Cost | € 2,415,658.78
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,073,391.79
|  |  |  | Total Investment Cost | € 5,042,103.82
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P141 | 66 | 246.53 | 90 | 21 | 5177.13
P144 | 66 | 266.25 | 110 | 28 | 7455
P146 | 54.9 | 450.96 | 75 | 17 | 7666.32
P149 | 110.2 | 228.43 | 225 | 100 | 22843
P174 | 450 | 1705.29 | 600 | 462 | 787843.98

## PACIFIC_RE
This sheet contains the results for tank connected to node: PACIFIC_RE
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 153.52 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 201.3 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,073.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9698.03 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.59 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 284.59 | m above nearest node |  | Tank Cost | € 2,626,973.96
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,765,189.13
|  |  |  | Total Investment Cost | € 6,945,216.35
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P134 | 277.6 | 448.9 | 500 | 348 | 156217.2
P135 | 220.4 | 359.13 | 500 | 348 | 124977.24
P141 | 66 | 246.53 | 140 | 41 | 10107.73
P142 | 123.4 | 294.61 | 140 | 41 | 12079.01
P144 | 66 | 266.25 | 160 | 52 | 13845
P146 | 54.9 | 450.96 | 200 | 79 | 35625.84
P149 | 110.2 | 228.43 | 200 | 79 | 18045.97
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P190 | 176.2 | 674.15 | 500 | 348 | 234604.2
P191 | 123.4 | 2102.35 | 500 | 348 | 731617.8
P192 | 110.2 | 908.41 | 125 | 34 | 30885.94
P193 | 54.9 | 439.45 | 125 | 34 | 14941.3

## J131
This sheet contains the results for tank connected to node: J131
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.43 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.17 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,044.12 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9628.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.79 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.79 | m above nearest node |  | Tank Cost | € 2,621,405.69
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,373,213.10
|  |  |  | Total Investment Cost | € 6,547,672.05
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P136 | 220.4 | 895.81 | 500 | 348 | 311741.88
P137 | 220.4 | 298.6 | 500 | 348 | 103912.8
P138 | 198.2 | 292.77 | 500 | 348 | 101883.96
P139 | 176.2 | 222.42 | 225 | 100 | 22242
P140 | 141 | 491.38 | 225 | 100 | 49138
P141 | 66 | 246.53 | 200 | 79 | 19475.87
P142 | 123.4 | 294.61 | 225 | 100 | 29461
P143 | 198.2 | 520.83 | 225 | 100 | 52083
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P145 | 220.4 | 992.43 | 315 | 190 | 188561.7
P146 | 54.9 | 450.96 | 90 | 21 | 9470.16
P149 | 110.2 | 228.43 | 160 | 52 | 11878.36
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 160 | 52 | 47237.32
P193 | 54.9 | 439.45 | 160 | 52 | 22851.4

## J132
This sheet contains the results for tank connected to node: J132
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.09 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.17 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,036.02 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9609.57 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.68 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 244.68 | m above nearest node |  | Tank Cost | € 2,349,378.47
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 900,715.95
|  |  |  | Total Investment Cost | € 4,803,147.68
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P141 | 66 | 246.53 | 75 | 17 | 4191.01
P144 | 66 | 266.25 | 90 | 21 | 5591.25
P146 | 54.9 | 450.96 | 63 | 14 | 6313.44
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63
P151 | 400 | 251.18 | 500 | 348 | 87410.64
P174 | 450 | 1705.29 | 600 | 462 | 787843.98

## J133
This sheet contains the results for tank connected to node: J133
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.06 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 201.17 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,035.49 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9608.3 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 294.3 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 254.3 | m above nearest node |  | Tank Cost | € 2,416,284.88
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 1,303,688.07
|  |  |  | Total Investment Cost | € 5,273,026.21
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P140 | 141 | 491.38 | 160 | 52 | 25551.76
P141 | 66 | 246.53 | 125 | 34 | 8382.02
P142 | 123.4 | 294.61 | 140 | 41 | 12079.01
P144 | 66 | 266.25 | 160 | 52 | 13845
P146 | 54.9 | 450.96 | 160 | 52 | 23449.92
P149 | 110.2 | 228.43 | 400 | 253 | 57792.79
P150 | 277.6 | 974.01 | 450 | 295 | 287332.95
P151 | 400 | 251.18 | 500 | 348 | 87410.64
P174 | 450 | 1705.29 | 600 | 462 | 787843.98

## CROCODILE_
This sheet contains the results for tank connected to node: CROCODILE_
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.31 | m |  | Minimum Pressure | 20.08 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.23 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,041.74 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9623.2 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.85 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.85 | m above nearest node |  | Tank Cost | € 2,621,821.47
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,199,506.55
|  |  |  | Total Investment Cost | € 6,374,381.28
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P134 | 277.6 | 448.9 | 600 | 462 | 207391.8
P135 | 220.4 | 359.13 | 600 | 462 | 165918.06
P141 | 66 | 246.53 | 125 | 34 | 8382.02
P142 | 123.4 | 294.61 | 125 | 34 | 10016.74
P144 | 66 | 266.25 | 160 | 52 | 13845
P146 | 54.9 | 450.96 | 200 | 79 | 35625.84
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P190 | 176.2 | 674.15 | 600 | 462 | 311457.3
P192 | 110.2 | 908.41 | 140 | 41 | 37244.81
P193 | 54.9 | 439.45 | 140 | 41 | 18017.45

## PORT
This sheet contains the results for tank connected to node: PORT
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.42 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 21 | hrs
Actual average pumped flow: | 201.16 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,044.23 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9629.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 293.8 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 283.8 | m above nearest node |  | Tank Cost | € 2,621,434.13
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 2,301,161.02
|  |  |  | Total Investment Cost | € 6,475,648.41
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P132 | 450 | 696.57 | 500 | 348 | 242406.36
P133 | 400 | 1011.47 | 500 | 348 | 351991.56
P134 | 277.6 | 448.9 | 500 | 348 | 156217.2
P135 | 220.4 | 359.13 | 500 | 348 | 124977.24
P136 | 220.4 | 895.81 | 250 | 120 | 107497.2
P137 | 220.4 | 298.6 | 315 | 190 | 56734
P141 | 66 | 246.53 | 160 | 52 | 12819.56
P142 | 123.4 | 294.61 | 160 | 52 | 15319.72
P144 | 66 | 266.25 | 200 | 79 | 21033.75
P146 | 54.9 | 450.96 | 125 | 34 | 15332.64
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63
P174 | 450 | 1705.29 | 600 | 462 | 787843.98
P192 | 110.2 | 908.41 | 500 | 348 | 316126.68
P193 | 54.9 | 439.45 | 315 | 190 | 83495.5

## R_HERA_2
This sheet contains the results for tank connected to node: R_HERA_2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 157.05 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 201.18 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,167.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9923.43 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 298.1 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 18.1 | m above nearest node |  | Tank Cost | € 773,608.22
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 24,396.33
|  |  |  | Total Investment Cost | € 2,351,057.81
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P141 | 66 | 246.53 | 75 | 17 | 4191.01
P144 | 66 | 266.25 | 75 | 17 | 4526.25
P146 | 54.9 | 450.96 | 63 | 14 | 6313.44
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63

## R_HERA_1
This sheet contains the results for tank connected to node: R_HERA_1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 157.04 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 201.17 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,167.50 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9922.61 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 298.11 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 28.11 | m above nearest node |  | Tank Cost | € 843,254.11
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 24,396.33
|  |  |  | Total Investment Cost | € 2,420,703.70
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P141 | 66 | 246.53 | 75 | 17 | 4191.01
P144 | 66 | 266.25 | 75 | 17 | 4526.25
P146 | 54.9 | 450.96 | 63 | 14 | 6313.44
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63

## prv1
This sheet contains the results for tank connected to node: prv1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 152.07 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 23 | hrs
Actual average pumped flow: | 201.18 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,035.85 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 9609.15 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 296.02 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 236.02 | m above nearest node |  | Tank Cost | € 2,289,121.36
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 812,240.31
|  |  |  | Total Investment Cost | € 4,654,414.93
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P141 | 66 | 246.53 | 75 | 17 | 4191.01
P144 | 66 | 266.25 | 75 | 17 | 4526.25
P146 | 54.9 | 450.96 | 63 | 14 | 6313.44
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63
P174 | 450 | 1705.29 | 600 | 462 | 787843.98

## 1
This sheet contains the results for tank connected to node: 1
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 158.45 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 201.23 | L/s |  | Critical Hour | 7 | hrs
Actual average pumped flow: | 201.17 | L/s |  | Critical Node | R_HERA_2
Cost: | € 4,205.06 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 10012.04 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 305.95 | m above sea level |  | Pump Cost | € 1,553,053.26
Tank height above ground | 154.95 | m above nearest node |  | Tank Cost | € 1,725,336.88
Tank volume | 2318.2 | m3 |  | Total Pipe Replacement Cost | € 617,837.25
|  |  |  | Total Investment Cost | € 3,896,227.39
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
P141 | 66 | 246.53 | 75 | 17 | 4191.01
P144 | 66 | 266.25 | 75 | 17 | 4526.25
P146 | 54.9 | 450.96 | 63 | 14 | 6313.44
P149 | 110.2 | 228.43 | 140 | 41 | 9365.63
P174 | 450 | 1705.29 | 500 | 348 | 593440.92