## Summary
Summary of results for tank connected to each node
Column1 | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc) | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
1 | pump3 | 0 | 20.49 | 5.7 | 5.71 | 15.27 | 36.35 | 78.18 | 38.18 | 65.63 | 20.1 | 22 | J108 | [] | 89698.48 | 317362.37 | 0 | 407060.85 | 4332.87 | 35489.42 | 45395.49
0 | J108 | 2.6 | 20.49 | 5.7 | 5.71 | 15.27 | 36.36 | 78.1 | 18.1 | 65.63 | 20.1 | 22 | J108 | [] | 89698.48 | 313408.88 | 0 | 403107.37 | 4301.24 | 35144.74 | 45019.76
1
[22 empty] | Node | Max Water Age (h) | Duty Head (m) | Duty Flow (L/s) | Actual average pumped flow (L/s) | Cost (€ /day) | Energy (kWh/day) | Tank Elevation (metres above sea level) | Tank height above ground (metres above nearest node) | Tank Volume (m3) | Minimum Pressure (mwc)
[22 empty] | J108 | 2.6 | 20.49 | 5.7 | 5.71 | 15.27 | 36.36 | 78.1 | 18.1 | 65.63 | 20.1
[22 empty] | pump3 | 0 | 20.49 | 5.7 | 5.71 | 15.27 | 36.35 | 78.18 | 38.18 | 65.63 | 20.1
[22 empty] | Node | Critical Hour (hrs) | Critical Node | Critical Pipes (list) | Pump Investment Cost (Capital Investment) | Tank Investment Cost (Capital Investment) | Total Pipe Replacement Cost (Capital Investment) | Total Investment Cost (Grand Total) | Maintenance Cost (pa) | Annuity (pa) | Total Annual Expenditure
[22 empty] | J108 | 22 | J108 | [] | 89698.48 | 313408.88 | 0 | 403107.37 | 4301.24 | 35144.74 | 45019.76
[22 empty] | pump3 | 22 | J108 | [] | 89698.48 | 317362.37 | 0 | 407060.85 | 4332.87 | 35489.42 | 45395.49

## J108
This sheet contains the results for tank connected to node: J108
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 20.49 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 5.7 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 5.71 | L/s |  | Critical Node | J108
Cost: | € 15.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 36.36 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 78.1 | m above sea level |  | Pump Cost | € 89,698.48
Tank height above ground | 18.1 | m above nearest node |  | Tank Cost | € 313,408.88
Tank volume | 65.63 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 403,107.37
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost

## pump3
This sheet contains the results for tank connected to node: pump3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 20.49 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 5.7 | L/s |  | Critical Hour | 22 | hrs
Actual average pumped flow: | 5.71 | L/s |  | Critical Node | J108
Cost: | € 15.27 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 36.35 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 78.18 | m above sea level |  | Pump Cost | € 89,698.48
Tank height above ground | 38.18 | m above nearest node |  | Tank Cost | € 317,362.37
Tank volume | 65.63 | m3 |  | Total Pipe Replacement Cost | € 0.00
|  |  |  | Total Investment Cost | € 407,060.85
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost