## Summary
Summary of results for tank connected to each node

## 2
This sheet contains the results for tank connected to node: 2
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.66 | m |  | Minimum Pressure | 20.1 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.66 | L/s |  | Critical Node | 30
Pumping Cost: | € 6,824.78 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16249.48 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 72.54 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 42.54 | m above nearest node |  | Tank Investment Cost | € 3,034,778.12
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 1,593,472.50
|  |  |  | Total Investment Cost | € 10,706,700.29
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
1 | 1016 | 100 | 1200 | 1098 | 109800
2 | 1016 | 1350 | 1200 | 1098 | 1482300
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 3
This sheet contains the results for tank connected to node: 3
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 46.93 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 30
Pumping Cost: | € 6,864.17 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16343.27 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 70.74 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 40.74 | m above nearest node |  | Tank Investment Cost | € 2,981,505.26
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 9,061,327.43
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 4
This sheet contains the results for tank connected to node: 4
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 48.49 | m |  | Minimum Pressure | 20.09 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 30
Pumping Cost: | € 7,083.25 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 16864.87 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 70.43 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 40.43 | m above nearest node |  | Tank Investment Cost | € 2,972,165.69
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 9,051,987.86
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 5
This sheet contains the results for tank connected to node: 5
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 50.11 | m |  | Minimum Pressure | 20.01 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 30
Pumping Cost: | € 7,310.77 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 17406.58 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 69.85 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 39.85 | m above nearest node |  | Tank Investment Cost | € 2,955,204.88
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 105,872.50
|  |  |  | Total Investment Cost | € 9,139,527.05
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
15 | 304.8 | 550 | 315 | 190 | 104500
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 6
This sheet contains the results for tank connected to node: 6
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 51.96 | m |  | Minimum Pressure | 19.95 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 30
Pumping Cost: | € 7,570.73 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18025.55 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 69.43 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 39.43 | m above nearest node |  | Tank Investment Cost | € 2,942,863.01
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 58,372.50
|  |  |  | Total Investment Cost | € 9,079,685.18
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
27 | 304.8 | 300 | 315 | 190 | 57000
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 7
This sheet contains the results for tank connected to node: 7
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 52.58 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 30
Pumping Cost: | € 7,657.40 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18231.91 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 69.47 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 39.47 | m above nearest node |  | Tank Investment Cost | € 2,943,963.24
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 1,372.50
|  |  |  | Total Investment Cost | € 9,023,785.41
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 8
This sheet contains the results for tank connected to node: 8
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 52.63 | m |  | Minimum Pressure | 20.04 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 20 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 22
Pumping Cost: | € 7,662.84 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18244.86 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 68.88 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 38.88 | m above nearest node |  | Tank Investment Cost | € 2,926,433.48
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 143,872.50
|  |  |  | Total Investment Cost | € 9,148,755.65
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
28 | 304.8 | 750 | 315 | 190 | 142500
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 9
This sheet contains the results for tank connected to node: 9
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 53.18 | m |  | Minimum Pressure | 20.02 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 19 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 22
Pumping Cost: | € 7,739.61 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18427.63 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 68.87 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 38.87 | m above nearest node |  | Tank Investment Cost | € 2,926,305.08
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 148,872.50
|  |  |  | Total Investment Cost | € 9,153,627.26
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
14 | 406.4 | 500 | 450 | 295 | 147500
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 10
This sheet contains the results for tank connected to node: 10
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 52.24 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 19 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 22
Pumping Cost: | € 7,603.31 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18103.12 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 67.06 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 37.06 | m above nearest node |  | Tank Investment Cost | € 2,872,728.31
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 341,872.50
|  |  |  | Total Investment Cost | € 9,293,050.48
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
13 | 406.4 | 800 | 450 | 295 | 236000
15 | 304.8 | 550 | 315 | 190 | 104500
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 11
This sheet contains the results for tank connected to node: 11
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 53.18 | m |  | Minimum Pressure | 19.91 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 19 | hrs
Actual average pumped flow: | 1107.78 | L/s |  | Critical Node | 22
Pumping Cost: | € 7,736.29 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18419.73 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 67.73 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 37.73 | m above nearest node |  | Tank Investment Cost | € 2,892,658.85
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 696,772.50
|  |  |  | Total Investment Cost | € 9,667,881.02
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
10 | 762 | 950 | 800 | 732 | 695400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5

## 12
This sheet contains the results for tank connected to node: 12
Pumping Parameters |  |  |  | Network Critical Results
Duty Head | 54.77 | m |  | Minimum Pressure | 20.06 | mwc
Duty Flow | 1107.78 | L/s |  | Critical Hour | 19 | hrs
Actual average pumped flow: | 1107.99 | L/s |  | Critical Node | 22
Pumping Cost: | € 7,965.48 | Euro per day |  | Critical Pipes | [] | Unit headloss >10m/km
Energy: | 18965.44 | kWh/day
Balancing Tank Parameters |  |  |  | Investment Cost Summary
Elevation | 68.94 | m above sea level |  | Pump Investment Cost | € 6,078,449.67
Tank height above ground | 38.94 | m above nearest node |  | Tank Investment Cost | € 2,928,201.18
Tank volume | 9850.38 | m3 |  | Total Pipe Replacement Cost | € 879,772.50
|  |  |  | Total Investment Cost | € 9,886,423.35
Table of individual pipes to be replaced
Pipe_name | Original_Diameter | Length | New_Diameter (mm) | Supply_and_Installed_Cost ($ USD/m) | Replacement_Cost
11 | 762 | 1200 | 800 | 732 | 878400
tank_connection |  | 1 | 1500 | 1372.5 | 1372.5